GALLANT  PROJECT SOLUTIONS LLC

Service-Disabled Veteran-Owned Small Business (SDVOSB)   ·   Veteran-Owned Small Business (VOSB)   ·   SBA Registered

SAMPLE

Requirements Intelligence Report™

CYCLE 1  ·  50% SCHEMATIC DESIGN

This is a sample Requirements Intelligence Report™ produced by Gallant Project Solutions LLC for demonstration purposes. The project — Heritage Health Campus / Northstar Ambulatory Care Clinic — is illustrative. The methodology, structure, register integrity, and analytical voice on every page that follows are exactly what Gallant produces on live client engagements.

Project name, organizations, and individuals have been replaced with generic references (Owner's PM, Architect of Record, CMAR, etc.) to protect the actual engagement. All other details — requirement counts, conflict counts, dollar figures, deadlines, regulatory citations, and the analytical structure of the report — is preserved exactly as Gallant produces it in live work.

Read this sample for:

·  What Gallant delivers at the 50% Schematic Design checkpoint, six months into a recurring monthly engagement.

·  What six months of work clears: 15 owner decisions closed, 4 design conflicts resolved, the project's cost variance brought back under the Board-authorized ceiling for the first time since baseline, and a complete audit trail showing who decided what, when.

·  What surfaces during design: the BIM coordination process catches two new clashes that would have become field rework if discovered after drawings were issued. The CMAR review surfaces two long-lead procurement decisions that the owner needs to make this month.

·  How the executive summary is written to be forwarded as-is to a project sponsor or capital partner: one paragraph on where the project stands, three named decisions the owner needs to act on, and a confidence indicator on the next gate.

Companion sample available. This sample shows what Gallant delivers at the 50% Schematic Design checkpoint, six months into a recurring monthly engagement. The companion Baseline sample shows the founding work this cycle built on. Reading both gives you the full picture: where the project started, and what six months of monthly engagement has cleared, opened, and surfaced. — Greg Tuite, PE PMP · Gallant Project Solutions LLC · May 2026

QUICK START GUIDE

How to read this report

What is this report? This is a Requirements Intelligence Report™ — Gallant's structured account of every binding requirement on the project, the conflicts and open decisions surfaced from those requirements, and the actions the owner needs to take before the next design gate. It is produced by reading every project document into a single registered list, then analyzing the list. The report is the same regardless of who reads it; the sections are organized so different readers can find what matters to them quickly.

Who reads what Executive (15 minutes). Read the front wrapper, the cover, and Section 2 (Executive Summary). That is the full picture at the level a sponsor or capital partner needs. Project Manager (45 minutes). Read Section 2, then Section 4.A (Owner Decision Register) for the actionable item list, then Section 5 for cost and schedule exposure. Section 9 (Cycle Comparison) shows what changed since the last report. Project Team (full read). All sections. Section 3 dashboard views, Section 4 priority items, Section 6 conflict register, and Section 7 document lineage are the working content. Appendix A documents Gallant’s self-disclosed quality findings.

Key terms used throughout GOVERNING. A requirement that is locked into the design basis. The design team is building to it. DECISION-PENDING. A requirement that is waiting on an owner action to lock. Until it closes, the design team cannot finalize that piece of the design. CONFLICT-PENDING. A requirement that is in conflict with another requirement. Both sides are documented; the conflict needs an owner-routed decision to resolve. Critical Impact. Gallant’s rating for any requirement where a change after design proceeds would force significant rework, schedule slip, or cost growth. Gallant considers a register healthy if no more than 30 percent of records carry this rating. Tier 1 / Tier 2 / Tier 3. How priority items are organized in Section 4. Tier 1 items must close before the next design gate. Tier 2 items need active management to prevent escalation. Tier 3 items are tracked but do not require executive attention this cycle.

Identifiers you will see throughout GR-XXXX. A requirement record. Every binding requirement on the project carries one of these. The number is sequential in the order requirements were added to the register. CF-XXX. A conflict record. Every conflict between two requirements carries one of these. D1, D2, ... D15. A source document. The number is sequential in the order Gallant processed the document into the register. Section 7 lists every document. DCM-HHC-NNN. A Decision Closure Memo. Every time an owner decision closes, Gallant issues one of these to document the decision and the audit trail back to the source.

Roles you will see throughout Owner's PM. The owner-side project manager. The decision owner on most items in the Owner Decision Register. AOR (Architect of Record). The lead architectural firm. Responsible for the overall design and for coordinating the design disciplines. SER (Structural Engineer of Record). The lead structural engineering firm. MEP-EOR (Mechanical, Electrical, Plumbing Engineer of Record). The lead MEP engineering firm. Some projects split this role across two or three firms. CMAR (Construction Manager At Risk). The general contractor under a CMAR delivery method, engaged during design to provide constructability input and pricing.

GALLANT  PROJECT SOLUTIONS LLC

Service-Disabled Veteran-Owned Small Business (SDVOSB)   ·   Veteran-Owned Small Business (VOSB)   ·   SBA Registered

REQUIREMENTS INTELLIGENCE REPORT

CYCLE 1 · 50% SCHEMATIC DESIGN

HERITAGE HEALTH CAMPUS

Northstar Ambulatory Care Clinic — Floors 1 & 2

| Report Date | July 18, 2025 |
| --- | --- |
| Run ID | HHC-REG-010 |
| Register Version | v2.0 (50% SD Baseline) |
| Prior Cycle | Baseline Run — Register v1.0 (January 28, 2025) |
| Cycle Window | January 28, 2025 → July 18, 2025 (24.4 weeks) |
| Methodology Version | Gallant Methodology v1.4 (May 2026) |
| Engagement Type | Recurring Monthly Engagement — Cycle 1 |
| Prepared By | Gallant Project Solutions LLC — Greg Tuite, PE PMP |
| Distribution | Owner, Owner's Rep, A/E Lead, CMAR Preconstruction |
| Quality Check (pre-report) | Workbook integrity check passed. 9 of 10 internal tests clear; 1 minor template item documented in Appendix A. |

© 2026 Gallant Project Solutions LLC. Proprietary and confidential. This Requirements Intelligence Report™ and the underlying methodology used to produce it are the proprietary intellectual property of Gallant Project Solutions LLC. Permitted use: solely for the authorized engagement to which it is delivered. Reproduction, adaptation, or redistribution outside the named engagement is prohibited without prior written consent from Gallant Project Solutions LLC.

Table of Contents

Section 1    ·    Project Snapshot

Section 2    ·    Executive Summary

Section 3    ·    Requirements Readiness Dashboard

Section 4    ·    Top Priority Items

4.A    ·    Owner Decision Register

4.B    ·    Scope Gaps

Section 5    ·    Cost and Schedule Exposure

Section 6    ·    Conflict Register Summary

Section 7    ·    Document Lineage Log

Section 8    ·    Next Cycle Dependencies

Section 9    ·    Cycle Comparison

Appendix A    ·    Workbook Integrity Findings

About this report. This is the first cycle report produced after the project's baseline. The Cycle Comparison section (Section 9) is the new content this cycle introduces — it shows what closed since baseline, what opened, and how the project's overall standing moved over six months.

# Section 1 — Project Snapshot

Establishes the register version and document set this report reflects. Structured data only; no narrative.

About the Requirements Register. The Requirements Register is the master list of the binding requirements the project must satisfy — program criteria, regulatory mandates, lease obligations, milestones, equipment specifications, and scope commitments, all in one place. Each entry carries a unique identifier (GR-XXXX), a source document, an owner, a criticality rating, and a verification status. The register is the single source of truth that owner, designer, contractor, and auditor can all read from. The other sections in this report draw from it. The register grew from 70 records at baseline to 124 records at this cycle as new source documents were processed.

| Field | Value |
| --- | --- |
| Report Date | July 18, 2025 |
| Cycle | Cycle 1 (50% SD Baseline) |
| Register Version | v2.0 (matches Lineage Log Entry 15) |
| Project Name | Heritage Health Campus — Northstar Ambulatory Care Clinic |
| Project Phase | Schematic Design complete — entering Design Development |
| Delivery Method | Hybrid — Base Building: CMAR (Cornerstone Construction); Tenant Improvement: A/E-led design with separate TI bid |
| Total Active Requirements | 124 (115 GOVERNING + 6 DECISION-PENDING + 3 CONFLICT-PENDING) |
| Total Documents Processed (cumulative) | 15 |
| Documents Processed This Cycle | 10 (D6 NMCBC, D7 A/E RFP, D8 Kickoff Minutes, D9 AHJ Response, D10 Geotech, D11 Owner Directives, D12 SD Outline Specs, D13 BIM Issues Log, D14 CMAR Review, D15 Cost Estimate) |
| Requirements Added This Cycle | 54 (GR-0071 through GR-0124) |
| Active Conflicts | 4 (CF-003, CF-006 carried from baseline; CF-007, CF-008 NEW from D13 BIM) |
| Conflicts Resolved This Cycle | 4 (CF-001, CF-002, CF-004, CF-005) |
| Open DECISION-PENDING Items | 8 (6 Open + 2 Overdue) |
| DECISION-PENDING Items Resolved This Cycle | 15 |
| Cycle Window | January 28, 2025 → July 18, 2025 (24.4 weeks elapsed) |
| Critical-Impact Concentration | 31 of 124 = 25.0% (under 30% ceiling) |
| Methodology Version | Gallant Methodology v1.4 (May 2026) |

AT-A-GLANCE

PROJECT KPIs AT CYCLE 1

Five-second view of the project's risk profile at the 50% Schematic Design checkpoint.

| Open Owner Decisions 8 ▼ down from 16 Down from 16 at baseline. Two are overdue at C1 close. | Active Conflicts 4 ▼ down from 6 Four resolved this cycle, two new from BIM coordination. |
| --- | --- |
| Critical-Impact Records 25% ▼ down from 30% Comfortably under the 30% ceiling Gallant considers healthy. | Cost Variance 4.4% ▼ down from 5.9% Below the 5% Value Engineering trigger for the first time. |

| CONFIDENCE ON NEXT GATE AMBER | Next gate (60% DD review, October 17, 2025): at risk. Three Tier 1 items must close in the next 8 weeks — two BIM-driven redesigns and the elevator engagement decision. None at impasse; all have named owners and resolution paths. The team has demonstrated capacity to clear gate-blockers in this cycle. |
| --- | --- |

# Section 2 — Executive Summary

How to read this section. This summary is written so it can be forwarded to a project sponsor or capital partner without modification. It opens with where the project stands, walks through the named decisions that need owner action this month, gives a confidence indicator on the next gate, and points into the rest of the report for the supporting detail.

## Where the Project Stands

This is the first cycle report after baseline for Heritage Health Campus. The cycle was strong — 15 of the 16 open owner decisions from baseline closed during this window, the four most contentious baseline conflicts resolved (MRI vendor selection, AHJ confirmation of FGI edition, geotechnical report received, generator scope allocated to the tenant), and the 50 percent Schematic Design cost estimate brought the project's cost variance to 4.4 percent — below the Board-authorized trigger threshold for the first time since baseline. The project completed Schematic Design and is positioned to enter Design Development. It is not yet positioned to close Design Development without resolving two new gate-blocking conflicts that surfaced in the BIM coordination run on July 11, plus two new long-lead procurement decisions surfaced in the CMAR constructability review on July 18. The next gate is the 60 percent Design Development review on October 17, 2025.

## Decisions That Must Close Before the Next Gate

Three findings below. Each is required for the 60 percent Design Development gate to close cleanly. The supporting register and conflict detail is in Section 4.

|  | Finding 1 — MRI Zone IV duct penetration and EES conduit routing must be redesigned before 60% DD. Condition. BIM Coordination Issues Log Rev 0.5 (July 11, 2025) identified two distinct compliance failures in the MEP coordination run. A supply air duct penetrates the ACR Zone IV magnetic field boundary at Grid C-4 without RF shielding — a non-compliance with the ACR Technical Standard. Three NFPA 99 Category 1 EES circuits are routed in normal-power conduit at Grid B-2 to D-4 — a Chapter 6 violation. Both items are documented as CF-008 in the conflict register and traced to register records GR-0115 (Zone IV duct) and GR-0118 (EES separation). Consequence. If not redesigned before the 60% DD coordination set is issued, the MEP narrative cannot be approved for DD release and the design carries a documented NFPA and ACR compliance failure into procurement scope. This is a multi-discipline rework event (Appendix A multi-discipline rework band, $150,000–$400,000) if the redesign is forced after subcontractor pricing. Resolved before 60% DD, the redesign is a coordination-level event handled inside the existing MEP fee. Owner and deadline. Decision owner: MEP Engineer of Record (MEP-EOR). Deadline: September 26, 2025 (3 weeks before 60% DD). Status. Items are open and have been logged through the BIM coordination process; MEP-EOR has acknowledged both clashes. Action required by September 26, 2025: MEP Engineer of Record (MEP-EOR) reroute the supply duct outside Zone IV or install an RF-shielded penetration at Grid C-4, and reroute the three EES circuits to physically separate red-coded conduit. If not closed by September 26, the multi-discipline rework cost band activates and the 60% DD coordination set carries the compliance failure into DD release. |
| --- | --- |

|  | Finding 2 — PT open-gym column at Grid E-5 must be evaluated for structural alternative before 60% DD. Condition. BIM Coordination Issues Log Rev 0.5 identified a 14-inch round concrete column at Grid E-5 sitting inside the 800-square-foot column-free zone required for the PT open gym (CF-007, GR-0003 ↔ GR-0116). Owner Program Criteria mandates the column-free zone; Structural Engineer of Record (SER)'s gravity-load model places the column there. The two requirements are irreconcilable without structural redesign. Consequence. If not evaluated before 60% DD, the structural narrative cannot be approved and the PT program carries a known program failure into DD release. The likely solution is a long-span post-tensioned transfer beam or long-span joist over the gym. Resolved at 30% DD analysis, this is a single-discipline redesign (Appendix A single-discipline redesign band, $40,000–$80,000) handled inside the structural fee. Resolved after structural drawings are issued for 60% DD, this becomes a multi-discipline rework event because the structural change cascades to MEP routing and architectural ceiling layout. Owner and deadline. Decision owner: Structural Engineer of Record (SER). Deadline: September 12, 2025 (5 weeks before 60% DD). Status. Item is open and has been logged through the BIM coordination process. Action required by September 12, 2025: Structural Engineer of Record (SER) evaluate long-span alternative at Grid E-5 and issue a written design directive selecting either the transfer beam or long-span joist solution. If not closed by September 12, the rework moves out of the structural fee window and the cost band escalates. |
| --- | --- |

|  | Finding 3 — Two long-lead procurement decisions opened at the CMAR constructability review require owner direction this month. Condition. CMAR Constructability Review (July 18, 2025) introduced two new DECISION-PENDING items with deadlines that have already passed: GR-0121 (generator pad location, due August 15) and GR-0122 (elevator contractor engagement, due September 1). The elevator item is the more consequential — the elevator package has a 52 to 64 week procurement lead, which means a contractor must be engaged during SD phase to support the construction-phase energize milestone in March 2027. Both items are now overdue at the report date and require immediate owner direction. Consequence. If the elevator contractor is not engaged within four weeks, the elevator package cannot be procured in time for construction sequencing, and the project schedule absorbs the slip directly. The cost consequence is project-specific and requires Cost Consultant scoping; the schedule consequence is non-negotiable. The generator pad location item is less consequential but is required before the gas service permit application can be submitted (GR-0120). Owner and deadline. Decision owners: Owner's PM for the elevator contractor; jointly with Cornerstone Construction (CMAR Preconstruction Lead) for the generator pad location. Status. Both items are flagged Overdue in the Decision Register. Action required immediately: Owner's PM issue written direction on the elevator contractor engagement path within 7 calendar days. The generator pad location should be confirmed in the same window so the gas service permit application can move forward. If not closed within the next two weeks, the elevator schedule risk becomes the dominant DD-phase critical path concern. |
| --- | --- |

## Confidence Indicator

AMBER. Next gate (60% DD review, October 17, 2025): at risk. Three Tier 1 items must close in the next 8 weeks for the gate to be achievable on schedule — two BIM-driven redesigns (CF-007 PT column, CF-008 Zone IV duct + EES) and the elevator contractor engagement decision. None of the three is at impasse; all have named owners, identified resolution paths, and documented escalation. The cycle behind us cleared 15 of 16 baseline DECISION-PENDING items in 24 weeks, which establishes the team's capacity to close gate-blockers — but the 8-week window to 60% DD is tighter than the prior cycle's pace, and CMAR-introduced procurement items can compound into schedule risk if elevator engagement slips.

## Where to Read More

Each finding above is supported by the records named in Section 4 (Top Priority Items) and the conflict detail in Section 6. The full Owner Decision Register with all 8 open items is in Section 4.A. Cost and schedule detail is in Section 5. Section 9 (Cycle Comparison) shows what closed since baseline, what opened, and how the project's overall standing moved over six months. Appendix A documents one workbook template item Gallant flagged for itself before the next cycle.

# Section 3 — Requirements Readiness Dashboard

Eight required dashboard views. Each view is a different lens on the same register: status, type, discipline, criticality, phase readiness, risk drivers, coordination hotspots, and decision-pending items. Tables and counts dominate; the brief notes are limited to a single sentence per view. Where a view shows an item that needs executive attention, the item is cross-referenced to Section 4 (Top Priority Items) for the detailed treatment.

View 1.  Status Distribution

Six DECISION-PENDING + 2 Overdue = 8 open owner-decision items. The two Overdue are Cycle 1 additions from CMAR constructability review (GR-0121, GR-0122).

| RequirementStatus | Count | VerificationStatus | Count | % of Active |
| --- | --- | --- | --- | --- |
| GOVERNING (Active) | 115 | Verified / Complete | 13 | 10% |
| DECISION-PENDING (Open) | 6 | In Progress | 32 | 26% |
| DECISION-PENDING (Overdue) | 2 | Not Started | 79 | 64% |
| CONFLICT-PENDING | 3 | Total Active | 124 | 100% |
| TOTAL Active | 124 | — | — | — |

View 2.  Type Breakdown

OMR (Operational & Maintenance) grew significantly this cycle from A/E RFP scope, raising O&M-tracked record count to 37 — the largest category.

| Requirement Type / Category | Count | Source Documents (cumulative through D15) |
| --- | --- | --- |
| FR — Functional Requirements | 8 | OPC Rev. 2, TJC Reg Summary |
| PR — Performance Requirements | 8 | OPC Rev. 2, TJC Reg, Equipment Schedule |
| SMR — Schedule & Milestone | 10 | Programming Doc, Milestone Schedule, A/E RFP, Kickoff |
| BCR — Budget & Cost | 8 | Programming Doc, A/E RFP, Cost Estimate |
| PIR — Physical & Interface | 27 | OPC, Equipment Schedule, NMCBC, AHJ Response, Geotech, BIM Issues, CMAR Review |
| RCR — Regulatory & Compliance | 23 | TJC Reg, NMCBC, AHJ Response, SD Outline Specs |
| SER — Sustainability & Environmental | 3 | OPC, Programming Doc, NMCBC |
| SLR — Security & Life-Safety | 5 | OPC, TJC Reg |
| OMR — Operational & Maintenance | 32 | OPC, A/E RFP, Equipment Schedule, SD Outline Specs |

View 3.  Discipline Breakdown

Architecture and MEP carry the largest record concentration. The CMAR coordination items added at SD close push CMAR/Construction Sequencing into a measurable cluster for the first time.

| Responsible Discipline (Lead) | Total | Open Decisions | % of Register | Critical-Impact Concentration |
| --- | --- | --- | --- | --- |
| Architecture (incl. shared) | 44 | 1 | 35% | Floor plans, MRI suite, AHC corridors, exam rooms (NM amendments), egress |
| Mechanical / HVAC / Controls | 16 | 2 | 13% | ASHRAE 170 isolation, MRI 24/7 cooling, Zone IV duct (CF-008) |
| Electrical / IT / Low-Voltage | 16 | 1 | 13% | EES Cat.1, ATS, generator allocation, EES conduit (CF-008) |
| Structural | 9 | 0 | 7% | MRI point load, PT column-free (CF-007), seismic SDC C |
| Plumbing | 7 | 1 | 6% | Hot water, med gas, floor drains, hand-wash sinks (ICRA) |
| Fire Protection | 3 | 0 | 2% | NFPA 13 separate clinical riser, egress |
| Cost Management | 8 | 0 | 6% | TPC, TI Allowance, generator allocation, escalation |
| CMAR / Construction Sequencing | 5 | 2 | 4% | MRI delivery opening, gas permit, generator pad, elevator (Tier 1) |
| Program Management / Regulatory | 8 | 1 | 6% | OPC issuance, accreditation, AHJ submittal, RIR conflict response |
| A/E Procurement / Contract | 8 | 0 | 6% | A/E licensure, deliverables structure, RFI/submittal cadence |

View 4.  Criticality Distribution

Critical Impact at 25 percent — comfortably under the 30 percent ceiling Gallant considers healthy. ('Critical Impact' is Gallant's rating for any requirement where a change after design proceeds would force significant rework, schedule slip, or cost growth.) Concentration dropped from 30 percent at baseline to 25 percent at SD close because the cycle added 54 records weighted toward High and Moderate categories.

| CriticalityCategory | Count | % of Register | Status Note |
| --- | --- | --- | --- |
| Critical | 31 | 25.0% | PASS — under 30% ceiling. Five new Critical at SD close (GR-0081, GR-0102, GR-0105, GR-0106, GR-0109, GR-0115, GR-0119, GR-0122, GR-0123, GR-0124). |
| High | 55 | 44.4% | Largest group. Concentrated in MEP, Architecture, A/E procurement scope. |
| Moderate | 30 | 24.2% | NMCBC additions weighted to Moderate. |
| Low | 8 | 6.4% | A/E procurement administrative items. |
| TOTAL | 124 | 100% | All records carry assigned ChangeImpactLevel. |

View 5.  Phase Readiness Indicator

Project completed SD with 13 verified records. 8 DECISION-PENDING items remain — must reach 0 by 60% DD authorization.

| Metric | Value | Interpretation |
| --- | --- | --- |
| Records Verified | 13 (10%) | Includes OPC issuance, AHJ pre-app, geotech, MRI vendor, generator allocation, AHC occupancy, FGI 2018 confirmation. |
| Records In Progress | 32 (26%) | Active SD-DD verification cycle records. |
| Records Not Started | 79 (64%) | Expected for DD/CD-phase verification work. |
| Open owner decisions | 8 | Down from 16 at baseline. Two are CMAR additions overdue at C1 close. |
| Active conflicts | 4 | CF-003 AHU, CF-006 STC 60 carry from baseline. CF-007 PT column, CF-008 Zone IV duct + EES are NEW from D13 BIM. |
| Critical-impact open | 31 (25.0%) | Under 30% ceiling. Healthy register profile. |
| Phase gate posture | 60% DD on track to AMBER | 8-week window. Three Tier 1 items must close. See Section 2 confidence indicator. |

View 6.  Risk Driver Clusters

Six clusters carry three or more Critical/High records. The Multi-Discipline Coordination cluster grew this cycle from BIM coordination findings.

| Risk Driver Cluster | Count | Critical / High | Escalation Note |
| --- | --- | --- | --- |
| Regulatory Approval / AHJ | 30 | 8 / 18 | TJC, NFPA, FGI 2018, NMCBC, NM amendments. AHJ responded — chain partially unblocked. |
| Life Safety | 18 | 9 / 8 | Egress, EES Cat.1, isolation rooms, MRI Zone IV (CF-008). |
| Multi-Discipline Coordination | 23 | 7 / 13 | MRI cluster (vendor confirmed), CF-007, CF-008, AHU scope, OFE inputs. |
| High-Cost Infrastructure | 16 | 6 / 9 | Generator (allocated to Northstar), MRI, EES, acoustic overlay, elevator package. |
| Long Lead | 10 | 5 / 5 | Generator (procurement gate Oct 31), elevator (52-64 wk lead — Tier 1), AHU lead, RF shielding. |
| AHJ Dependency (sub-cluster) | 3 | 2 / 1 | AHJ pre-app closed; FGI 2018 + NM amendments now in design basis. |
| Decision Required | 8 | 4 / 4 | All 8 open DECISION-PENDING items. Down from 16 at baseline. |
| Construction Sequencing (Cycle 1 NEW) | 5 | 3 / 2 | MRI delivery opening (GR-0119), elevator engagement (GR-0122), gas permit (GR-0120), generator pad (GR-0121), meter coordination. |

View 7.  Coordination Hotspots

Two new hotspots emerged this cycle from the BIM coordination run. The MRI cluster has matured from a vendor-decision hotspot to a delivery-sequencing hotspot.

| Discipline Pairing | Records | Critical Items | Hotspot Description |
| --- | --- | --- | --- |
| Architecture × Structural | 7 | 4 | PT column-free (CF-007), MRI structural (resolved Siemens), AHC corridor, MRI delivery wall. |
| MEP × Architecture × Life Safety | 5 | 3 | MRI Zone IV duct (CF-008), EES separation (CF-008), isolation room HVAC. |
| Mechanical × Cost | 4 | 2 | AHU scope (CF-003), AHU long-lead, generator (resolved). |
| Architecture × CMAR Sequencing | 4 | 3 | MRI delivery opening, elevator engagement, generator pad, gas permit timing. |
| Architecture × NM-AHJ | 8 | 4 | FGI 2018 + NM amendments: 120 NSF exam rooms, 8-ft AHC corridors, NFPA 101 Ch. 20 egress. |
| BIM × MEP × Structural | 6 | 3 | BIM coordination cycle: CF-007, CF-008, MRI suite layout, transfer beam. |
| IT × Electrical × A/V | 5 | 0 | PACS, UPS, AV closet, telemedicine — A/E RFP and Kickoff added 4 records. |

View 8.  DECISION-PENDING Status

Eight open items down from 16 at baseline. Two are NEW Cycle 1 additions from CMAR review and are already overdue at C1 close — both are flagged in Section 4 (the elevator decision in Tier 1, the generator pad in Tier 2) because Gallant treats overdue procurement decisions as gate-blocking regardless of their original criticality rating.

| DecisionType | Open Count | Overdue | Owner Action Required |
| --- | --- | --- | --- |
| TBD-UNRESOLVED | 2 | 0 | GR-0019 ICRA (Northstar Infection Preventionist), GR-0038 medical gas locations (Northstar Clinical Director) |
| CONDITIONAL | 4 | 0 | GR-0022 generator procurement, GR-0023 RF shielding contractor, GR-0051 hand-wash sink placement, GR-0056 Cat.1 EES sizing |
| EMBEDDED-CHOICE | 0 | 0 | All baseline EMBEDDED-CHOICE items resolved (MRI vendor, AHU scope direction). |
| SHOULD-LANGUAGE | 0 | 0 | None at baseline; none introduced this cycle. |
| Cycle 1 NEW | 2 | 2 | GR-0121 generator pad location (Overdue Aug 15), GR-0122 elevator contractor engagement (Overdue Sep 1). |
| TOTAL OPEN | 8 | 2 | Target: 0 by 60% DD gate (October 17, 2025). 13 weeks remaining. |

Phase Gate Compliance Rule. All 8 open owner decisions must be marked Resolved before Gallant will recommend the project move into the next gate. Two items (GR-0121, GR-0122) appear in Section 4 — the elevator decision in Tier 1 (gate-blocking), the generator pad in Tier 2 (high-priority management). Gallant treats overdue procurement decisions as gate-blocking regardless of their original criticality rating.

# Section 4 — Top Priority Items

Items needing executive attention are organized into three tiers. Tier 1 items are gate-blocking and receive full narrative treatment in both Section 2 (the executive view) and Section 4.1 below (the detailed view with register IDs, source documents, and resolution path). Tier 2 items need active management to prevent escalation and appear in a summary table. Tier 3 items are tracked in the register but do not require executive attention this cycle.

## 4.0  Tier Summary

| Tier | Count | Cap (v1.4) | Format | Where Detailed |
| --- | --- | --- | --- | --- |
| Tier 1 — Gate-Blocking | 3 | 5 max | Full narrative | Section 2 + Section 4.1 |
| Tier 2 — High-Priority Coordination | 8 | 10 max | Summary table | Section 4.2 |
| Tier 3 — Tracked | 23 | — | Reference only | Workbook only |
| TOTAL Section 4 priority-qualifying | 34 | — | — | — |

Distribution interpretation: A modest Tier 1 count of three reflects the relative health of the register at this cycle — most baseline gate-blockers closed, and the three remaining items are well-defined with named owners. Tier 2 holds the cluster of long-lead procurement and AHJ-dependent items still working through resolution chain. Tier 3 includes all NM Commercial Building Code records, A/E RFP procurement records, and supplemental records added by the Kickoff Minutes — tracked in the register but not gate-blocking.

## 4.1  Tier 1 — Gate-Blocking Decisions  (Detailed View)

The Section 2 view is the executive narrative. The Section 4.1 view below adds the supporting detail: which records in the register the finding draws from, which source documents the finding is grounded in, the qualification rule that placed the item in Tier 1, the disposition path to resolution, and any downstream cascade.

### Tier 1 — Item 1.  CF-008: MRI Zone IV duct + EES conduit redesign

| Form B Field | Content |
| --- | --- |
| Register identifiers | GR-0115 (Zone IV duct, CONFLICT-PENDING), GR-0118 (EES separation, CONFLICT-PENDING) |
| Conflict cross-references | CF-008 (ParameterConflict — closes with this redesign) |
| Source documents | AOR 50% SD BIM Coordination Issues Log Rev 0.5 (D13, July 11, 2025), GR-0049 ACR Technical Standard MRI siting (D1), GR-0045 NFPA 99 (D1) |
| Tier 1 qualification rule | Active conflict (CF-008) where resolution requires owner-routed action and at least one of the two requirements in conflict carries a Critical change-impact rating. GR-0115 is Critical. |
| Disposition path | MEP Engineer of Record (MEP-EOR) issues design directive memo selecting one of: (a) reroute supply duct outside Zone IV; (b) provide RF-shielded penetration at Grid C-4 (vendor and spec to be coordinated with RF shielding contractor under GR-0023). Concurrent: reroute three EES circuits to physically separate red-coded conduit. On receipt of directive, Gallant updates GR-0115 and GR-0118 to GOVERNING and issues a Decision Closure Memo. |
| Downstream records | Closes 0 CONDITIONAL records directly but unblocks the 60% DD MEP narrative finalization. Does not affect CF-007 (PT column) or any baseline open items. |

### Tier 1 — Item 2.  CF-007: PT open-gym structural alternative at Grid E-5

| Form B Field | Content |
| --- | --- |
| Register identifiers | GR-0003 (PT open gym 800 SF column-free, GOVERNING), GR-0116 (BIM clash BIM-010, CONFLICT-PENDING) |
| Conflict cross-references | CF-007 (ScopeConflict — closes with structural redesign directive) |
| Source documents | Owner Program Criteria Rev. 2 (D2), AOR 50% SD BIM Coordination Issues Log Rev 0.5 (D13) |
| Tier 1 qualification rule | Active conflict (CF-007) where resolution requires owner-routed structural decision and at least one of the two requirements in conflict carries a Critical change-impact rating (GR-0003 is Critical for program compliance). |
| Disposition path | Structural Engineer of Record (SER) evaluates two alternatives: (a) post-tensioned transfer beam carrying gravity loads outside the column-free zone; (b) long-span joist solution. Issues written design directive selecting alternative with cost rough-order-of-magnitude by September 12, 2025. On receipt, Gallant updates GR-0116 to GOVERNING (with the alternative as design basis) and issues Decision Closure Memo. Cost impact included in BCR-004 VE review at 60% DD. |
| Downstream records | Closes 0 CONDITIONAL records but unblocks 60% DD structural narrative finalization. Has secondary cascades to MEP routing in the gym ceiling (review at 60% DD coordination). |

### Tier 1 — Item 3.  Elevator contractor engagement (GR-0122) — long-lead procurement

| Form B Field | Content |
| --- | --- |
| Register identifiers | GR-0122 (Elevator contractor engagement, DECISION-PENDING — Overdue, due September 1, 2025) |
| Conflict cross-references | None (this is a procurement decision, not a conflict). |
| Source documents | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 (D14, July 18, 2025) |
| Tier 1 qualification rule | Overdue decision deadline as of report date, regardless of original criticality rating. Plus: irreversible critical-path event with open dependency — the 52-64 week elevator lead time and the March 2027 construction-phase energize milestone. |
| Disposition path | Owner's PM issues written direction within 7 calendar days authorizing CMAR (Cornerstone Construction, CMAR Preconstruction Lead) to engage elevator contractor under early-procurement scope. Cornerstone responds with proposed elevator vendor and contract structure within 14 calendar days of authorization. On execution, Gallant updates GR-0122 to GOVERNING and issues Decision Closure Memo. |
| Downstream records | Closes 0 CONDITIONAL records but unblocks construction-phase elevator energize milestone. Schedule cost is non-negotiable; cost consequence requires Cost Consultant scoping if procurement slips beyond October 1, 2025. |

## 4.2  Tier 2 — High-Priority Coordination Items

Critical or high-impact records that are not currently gate-blocking but require active management to prevent escalation. Summary table only — no narrative treatment. Eight items at Cycle 1, within the v1.4 cap of 10.

| # | Req ID | Description | Tier 2 Rule | Owner / Deadline | Disposition Note |
| --- | --- | --- | --- | --- | --- |
| 1 | GR-0042 | TJC AHC accreditation framework (52 sub-requirements) | Critical+Open / DesignDriver | Northstar Compliance / Day-1 ops | Top-level driver. Rolls forward to every cycle. |
| 2 | GR-0019 | ICRA delivery — HVAC zones, sink placement | Critical+Open / no decision pending owner | Northstar Infection Prev. / Sep 5 | Hand-sink placement (GR-0051) chains. ICRA expected Sep 5. |
| 3 | GR-0022 | Generator procurement initiation | LongLead+CONDITIONAL | Cornerstone CMAR / Oct 31, 2025 | Generator scope resolved (D11). Procurement now an executable item. |
| 4 | GR-0121 | Generator pad location confirmation | Overdue / CMAR-introduced | Owner's PM + CMAR Preconstruction Lead / Aug 15 (overdue) | Auto-escalated per v1.4 §4. Required before gas permit (GR-0120). |
| 5 | CF-003 | Clinical AHU procurement scope (Heritage vs. Northstar) | Active conflict, both sides High | Owner's PM + Tenant Facilities Lead / 60% DD | Lease side letter pending. AHU 12-18 wk lead. |
| 6 | CF-006 | STC 60 acoustic overlay scope and cost | Active conflict, both sides High | Owner's PM + Tenant Facilities Lead / 60% DD | Acoustic subconsultant analysis at 30% DD per GR-0117. |
| 7 | GR-0023 | RF shielding contractor engagement | LongLead+CONDITIONAL | Northstar / GC Pre-Con / Oct 31 | Spec dependent on Siemens basis (GR-0109). 12-week minimum lead. |
| 8 | GR-0102 | NM DOH 90% CD plan review submission | Critical regulatory milestone | AOR / 90% CD | Establishes formal AHJ submittal date. Non-negotiable per AHJ response (D9). |

## 4.3  Tier 3 — Tracked Items

An additional 23 records meet Section 4 qualification triggers and are tracked in the Requirements Register with assigned ChangeImpactLevel and ResponsibleDiscipline. Categories: NM Commercial Building Code records (GR-0071 through GR-0081 — 11 records, primarily Moderate impact); A/E RFP procurement records (GR-0082 through GR-0093 — 9 records covering deliverables structure, RFI/submittal cadence, BIM coordination); cost reconciliation records (GR-0123, GR-0124 — TPC and TI Allowance tracking); foundation system records (GR-0107, GR-0108 from geotech); and AHJ-confirmed regulatory records (GR-0103, GR-0104, GR-0105, GR-0106). These are not gate-blocking and do not require executive attention this cycle.

## 4.A  Owner Decision Register

About the Owner Decision Register. The Owner Decision Register is the structured list of requirements currently waiting on an owner action to close. These are not Gallant deliverables — they are decisions the owner must make so the design team can finalize the design. Each entry is grouped by what kind of decision it is, and each carries a named decision owner and a deadline. This register is the single most actionable page in the report — it is the place an owner's PM looks first to see what is on their plate this cycle.

Cycle 1 status. Eight open DECISION-PENDING items at C1 close. Down from 16 at baseline — fifteen baseline items closed during this cycle. Two new items entered at C1 close (GR-0121, GR-0122) and are already overdue. The 4.A list below presents only the 8 currently open items grouped by decision type. The Cycle Comparison block in Section 9 documents the 15 baseline closures with Decision Closure Memo references.

### Group 1 — TBD-UNRESOLVED  (2 items)

|  | Req ID | Description | What Value Is Needed | Decision Owner | Deadline |
| --- | --- | --- | --- | --- | --- |
| ● | GR-0019 | ICRA — infection control risk assessment | Completed ICRA: HVAC zone boundaries, neg-pressure extents, sink placement | Northstar Infection Preventionist | September 5, 2025 |
| ● | GR-0038 | Medical gas additional locations (OAI-004) | Northstar Clinical Director confirmation of additional med-gas outlet locations | Northstar Clinical Director | Prior to 60% DD |

### Group 2 — CONDITIONAL  (4 items)

|  | Req ID | Description | Upstream Dependency | Resolves When | Auto-Close? |
| --- | --- | --- | --- | --- | --- |
| ● | GR-0022 | Generator procurement initiation | Resolved by D11 generator allocation directive | PO authorized by Cornerstone | No — requires PO action |
| ● | GR-0023 | RF shielding contractor engagement | Resolved by D11 MRI vendor confirmation (Siemens) | Spec to shielding sub + contract | No — requires contract action |
| ● | GR-0051 | Hand-washing sink placement | GR-0019 (ICRA delivery) | ICRA received + reviewed | Yes — sink placement locks per ICRA |
| ● | GR-0056 | Category 1 EES — clinical ATS sizing | Resolved by D11 generator allocation (350 kW) | DD electrical narrative finalization | Yes — design basis locked |

### Group 3 — Cycle 1 NEW (Overdue at C1 close)  (2 items)

|  | Req ID | Description | What Must Happen to Close | Decision Owner | Deadline |
| --- | --- | --- | --- | --- | --- |
| ● | GR-0121 | Generator pad location confirmation | Confirm pad location in SD site plan drawings before gas service permit application (GR-0120 chain). CMAR memo + A/E confirmation drawing. | Owner's PM + CMAR Preconstruction Lead | OVERDUE — Aug 15, 2025 |
| ● | GR-0122 | Elevator contractor engagement during SD | 52-64 week elevator package lead. Engagement during SD required for March 2027 energize. Owner authorization for early-procurement scope. | Owner's PM | OVERDUE — Sep 1, 2025 |

Phase Gate Compliance — 4.A Closeout. Total open count (8) must reach zero before Gallant will recommend 60% DD authorization. Two overdue items (GR-0121, GR-0122) require immediate owner attention. Three of the four CONDITIONAL items now have their upstream parents resolved and are executable — they need procurement or design action, not further owner decisions.

## 4.B  Scope Gaps

No GAP-status records exist in the v2.0 register. Three records carry the SCOPE_GAP risk-driver flag — the carryover items from baseline (CF-003 AHU scope and CF-006 STC 60 acoustic overlay), plus the new generator pad coordination boundary (GR-0121). These are documented in conflict register and Tier 2.

# Section 5 — Cost and Schedule Exposure

Cycle 1 brought significant favorable movement in the cost picture. The 50% SD cost estimate (D15, Cost Consultant) closed the project's Total Project Cost (TPC) variance from 5.9 percent at baseline to 4.4 percent at SD close — below the 5 percent Value Engineering trigger threshold for the first time. Three named offsets contributed: VE-01 foundation savings ($240K confirmed by geotech), generator allocation directed to Northstar TI ($220K removed from base building exposure), and acoustic overlay scope still pending allocation. Two new schedule risks emerged this cycle from the CMAR review.

## 5.A  Cost Exposure

| Exposure Category | Identified Items at C1 Close | Supporting Records |
| --- | --- | --- |
| Total Project Cost variance | Current 50% SD estimate $71.0M against $68M Board ceiling — variance $3.0M (4.4%). Down from $4.0M (5.9%) at baseline. Below BCR-004 trigger threshold for the first time. Variance recovery driven by VE-01 confirmation and generator allocation closure. | GR-0027, GR-0123 (50% SD reconciliation, D15), GR-0030 (BCR-004), GR-0107 (geotech VE-01 unlock) |
| Confirmed cost reductions this cycle | VE-01 foundation system ($240K confirmed via geotech Site Class C confirmation) + generator upsize allocation directed to Northstar TI ($220K removed from base building exposure) = $460K aggregate variance recovery. | GR-0107 (geotech), GR-0111 (generator allocation D11), BCR-004 VE log |
| Open scope-allocation items | CF-003 AHU procurement scope ($150K-$280K range pending allocation) and CF-006 STC 60 acoustic overlay ($80K-$150K range, allocation pending). Both expected to resolve before 60% DD per Tier 2 disposition. | CF-003, CF-006, GR-0036, GR-0050 |
| Cycle 1 BIM-driven cost exposure | CF-007 (PT column) likely $40K-$80K (Appendix A single-discipline redesign band) if resolved before 60% DD, escalating if delayed. CF-008 (MRI Zone IV duct + EES) also single-discipline redesign band, escalating to multi-discipline rework band ($150K-$400K) if not resolved before 60% DD coordination set. | CF-007, CF-008, GR-0115, GR-0116, GR-0118 |
| TI Allowance utilization | Clinical TI allowance $14.2M binding. Current utilization $13,580,000 ($9,380,000 base TI construction + $1,750,000 medical equipment + $620,000 LASER/PT additions per D11 + $1,830,000 contingency). Headroom: $620,000. | GR-0028, GR-0124 (TI utilization tracking, D15) |
| DECISION-PENDING cost exposure | Six open DECISION-PENDING items carry cost implications: ICRA delivery (no direct dollar impact), medical gas additions (within TI), generator procurement (allocated), RF shielding (allocated), hand-sinks (within TI), Cat.1 EES sizing (within scope). Two new C1 items: generator pad (no incremental cost), elevator engagement (early-procurement structure to be determined by CMAR — Cost Consultant scoping recommended). | GR-0019, GR-0022, GR-0023, GR-0038, GR-0051, GR-0056, GR-0121, GR-0122 |

TPC Headline. Variance moved from $4.0M (5.9%) at baseline to $3.0M (4.4%) at 50% SD. Below the BCR-004 5% trigger. Two new BIM-driven cost risks (CF-007, CF-008) are inside the cost range that single-discipline redesign can absorb if resolved before 60% DD. The favorable movement opens room to absorb CF-003 and CF-006 allocations without breaching the ceiling, but only if the 60% DD coordination set is clean.

## 5.B  Schedule Exposure

| Exposure Category | Identified Items at C1 Close | Supporting Records |
| --- | --- | --- |
| Input-dependent records | Eight open DECISION-PENDING items each block specific design or procurement milestones. Concentrated paths: ICRA (HVAC narrative), CF-007/CF-008 (60% DD coordination set), elevator (construction-phase energize), generator pad (gas permit chain). | All Section 4.A items |
| Long-lead procurement | Three procurement gates active: 350kW generator (PO by Oct 31, 2025 per GR-0022), elevator package (52-64 wk — engagement during SD required, GR-0122), AHU long-lead (12-18 wk pending CF-003 resolution), RF shielding (12 wk pending GR-0023 spec finalization). | GR-0022, GR-0122, GR-0023, CF-003 |
| Sequencing risks (irreversible) | MRI pre-enclosure construction sequence (GR-0024) — magnet must be set before wall enclosure. MRI delivery opening confirmed in CD per GR-0119. Construction-phase elevator energize (March 2027) — see GR-0122. Both are construction-phase critical path with no design-phase rollback. | GR-0024, GR-0119, GR-0122 |
| AHJ-driven schedule | NM DOH 90% CD plan review submission required (GR-0102). Establishes formal AHJ submittal date and creates a hard CD coordination deadline that backs into DD. RF shielding spec subject to NM DOH approval per GR-0104. | GR-0102, GR-0104 |
| Cycle 1 NEW schedule risks | Elevator engagement (Tier 1) and generator pad confirmation (Tier 2). Both introduced by CMAR review and overdue at C1 close. Elevator is the dominant DD-phase schedule risk if engagement slips beyond mid-September. | GR-0121, GR-0122 |

Schedule Headline. 60% DD on October 17, 2025 is the binary date for Cycle 2. Three Tier 1 items must close in the 8-week window. Two long-lead procurement items (generator, elevator) must execute on PO action with no further owner decisions required. Construction-phase critical path is intact — the SD-phase work has built the foundation for DD/CD. Recommend a weekly decision-burndown review through 60% DD and a long-lead procurement review at 30% DD.

Extended service available. Gallant's cost and schedule consulting partners can quantify each exposure category above as scoped add-on service: dollar-value estimates of identified exposures, requirements-driven earned value management through the full project lifecycle (design, construction, and commissioning), and schedule risk quantification tied to the requirements register.

# Section 6 — Conflict Register Summary

About the Conflict Register. The Conflict Register is the catalog of any place where two requirements in the project record contradict each other or compete for the same resource. Conflicts are a normal output of design — they surface when a regulatory mandate runs into a program criterion, when one document specifies one value and another document specifies a different value for the same item, or when a contract is silent on who is responsible for a piece of scope. Catching them in the requirements register before they become design rework is the value of the Conflict Register. Each conflict here carries a unique identifier (CF-XXX), the two requirements in conflict, a recommended resolution path, and a decision owner.

Eight conflicts have been logged on this project to date. A conflict is any place where two requirements in the register contradict each other or compete for the same resource. Four resolved during this cycle (CF-001, CF-002, CF-004, CF-005). Two carried from baseline are still open (CF-003, CF-006). Two new conflicts surfaced during the BIM coordination run (CF-007, CF-008). Net: 4 active conflicts at the close of this cycle, down from 6 at baseline. Two of the four active conflicts must be resolved before the next gate — they are documented in detail in Section 4.

Conflict lifecycle this cycle.  How the conflict count moved from baseline to Cycle 1.

| BASELINE 6 conflicts | → | RESOLVED −4 this cycle | → | CARRIED 2 still open | + | NEW +2 from BIM | = | CYCLE 1 4 active |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Conflict Type | Active Count | Records Affected |
| --- | --- | --- |
| ParameterConflict | 1 | CF-008 (Zone IV duct + EES) |
| ScopeConflict | 3 | CF-003 (AHU procurement), CF-006 (STC 60), CF-007 (PT column) |
| AuthorityConflict | 0 | CF-005 RESOLVED (FGI 2018 + NM amendments confirmed by NM DOH, D9) |
| MethodConflict | 0 | None detected at any cycle. |
| SequenceConflict | 0 | None detected at any cycle. |
| TOTAL ACTIVE | 4 | Down from 6 at baseline. Resolution paths owner-routed. |

## Active Conflicts — Detail

| CF-003 ScopeConflict OPEN (carried) | Requirements: GR-0036 ↔ GR-0028 What's happening: Clinical AHU procurement scope boundary. OPC §4.1 mandates dedicated clinical AHUs separate from base building HVAC. NNN Lease Exhibit D — the contractually controlling scope-allocation document — is silent on AHU procurement. Carried from baseline. D11 Owner Directives addressed generator allocation but did not address AHU scope. Value A: OPC §4.1: 'Northstar requires dedicated HVAC systems serving the clinical component, separate from the base building residential and retail systems' Value B: Programming Doc §C / NNN Lease Exhibit D — silent on clinical AHU procurement Recommended action: Owner's PM and Tenant Facilities Lead execute lease side letter or scope memo before 60% DD gate (October 17, 2025). CMAR cannot begin AHU procurement (12-18 wk lead) without scope assignment. Source documents: Owner Program Criteria Rev. 2 (D2) · Programming Document v1.0 (D3) / NNN Lease Exhibit D |
| --- | --- |

| CF-006 ScopeConflict OPEN (carried) | Requirements: GR-0050 ↔ GR-0031 What's happening: STC 60 / IIC 55 acoustic separation between Level 2 clinical and Level 3 residential. The 8-inch PT flat plate cannot achieve this rating alone. Acoustic overlay required ($80K-$150K range). Neither OPC nor Programming Doc allocates the cost. D11 Owner Directives did not address this allocation. D12 SD Outline Specs added GR-0117 (Level 3 residential acoustic floating floor design) which moves the acoustic responsibility into base building scope on technical grounds, but cost allocation remains unassigned. Value A: TJC Summary RQ-019: STC 60 / IIC 55 between Level 2 clinical and Level 3 residential Value B: Programming Doc / OPC — silent on acoustic overlay cost allocation Recommended action: Acoustic subconsultant confirms minimum assembly meeting STC 60 at 30% DD analysis per GR-0117. A/E identifies cost allocation (Heritage or Northstar) before 60% DD. Cost incorporated in BCR-004 VE review. Source documents: TJC Regulatory Requirements Summary (D1) · Owner Program Criteria Rev. 2 (D2) |
| --- | --- |

| CF-007 ScopeConflict NEW | Requirements: GR-0003 ↔ GR-0116 What's happening: PT open gym column at Grid E-5. PIR requirement mandates 800 SF column-free PT open gym (GR-0003). BIM clash BIM-010 from 50% SD coordination run shows a 14-inch round concrete column at Grid E-5 within the required column-free zone. Program requirement and structural model are irreconcilable without design revision. Tier 1 gate-blocker — see Section 4.1 Item 2. Value A: GR-0003: '800 SF column-free open gym' per Owner Program Criteria Value B: GR-0116 / BIM-010: '14-inch round concrete column at Grid E-5 within PT open gym' Recommended action: Structural Engineer of Record (SER) evaluates long-span alternative (post-tensioned transfer beam or long-span joist) at 30% DD. Issues written design directive selecting alternative by September 12, 2025. Structural revision required before 60% DD. Source documents: Owner Program Criteria Rev. 2 (D2) · AOR 50% SD BIM Coordination Issues Log Rev 0.5 (D13) |
| --- | --- |

| CF-008 ParameterConflict NEW | Requirements: GR-0115 ↔ GR-0118 What's happening: MRI Zone IV duct penetration and EES conduit routing — two distinct compliance failures in the same BIM coordination run. (1) Supply air duct penetrates ACR Zone IV magnetic field boundary at Grid C-4 without RF-shielded penetration. (2) Three NFPA 99 Category 1 EES circuits routed in normal-power conduit at Grid B-2 to D-4. Both items reduce to a Cycle 1 Tier 1 gate-blocker — see Section 4.1 Item 1. Value A: GR-0115 (ACR Zone IV): zero unshielded duct penetrations in Zone IV boundary Value B: GR-0118 (NFPA 99 Ch. 6): EES circuits physically separated from normal power Recommended action: MEP Engineer of Record (MEP-EOR) reroutes supply duct outside Zone IV OR provides RF-shielded penetration at Grid C-4. Concurrent: reroute three EES circuits to physically separate red-coded conduit. Both resolve before 60% DD coordination set issuance. Source documents: ACR Technical Standard (cited in TJC Reg D1) · AOR 50% SD BIM Coordination Issues Log Rev 0.5 (D13) |
| --- | --- |

## Conflicts Resolved This Cycle

| CF | Conflict | Resolution Path | Closure Document |
| --- | --- | --- | --- |
| CF-001 | Generator capacity (200 vs. 350 kW) | Resolved via D11 Owner Design Directive — Northstar funds 350 kW upsize ($220K from Northstar TI allowance). Combined-load requirement now in writing. | D11 / DCM-HHC-003 |
| CF-002 | MRI equipment room area (200 vs. 240 NSF) | Resolved via D11 Owner Design Directive — Siemens MAGNETOM Altea confirmed as design basis. 200 NSF locks per Siemens. Resolved in chain with CF-004. | D11 / DCM-HHC-001 |
| CF-004 | MRI structural point load (7,700 vs. 8,100 lb) | Resolved via D11 Owner Design Directive — Siemens 7,700 lb confirmed as structural design basis. Closes in chain with CF-002. | D11 / DCM-HHC-001 |
| CF-005 | FGI edition adoption (2022 vs. 2018) | Resolved via D9 NM CID/NM DOH AHJ Pre-Application Determination — NM DOH on FGI 2018 (NM amendments augment FGI 2018 with 120 NSF exam rooms, 8-foot AHC corridors, NFPA 101 Ch. 20 egress). FGI 2018 + NM amendments now in design basis. | D9 / DCM-HHC-002 |

Audit-trail note. Each resolution above corresponds to a Decision Closure Memo (DCM-HHC-001, -002, -003) issued during this cycle as part of Gallant's standard practice of documenting decision closures. The DCM identifiers are referenced in Section 9 Cycle Comparison and form the audit trail back to D9 (AHJ response) and D11 (Owner Design Directives) in the Document Lineage Log.

# Section 7 — Document Lineage Log

About the Document Lineage Log. The Document Lineage Log is the chronological record of the source documents Gallant has processed into the project's requirements register, in the order they were processed. Each entry shows the document name, its version, when it was issued, when it was processed, how many requirements it added to the register, and whether it surfaced any conflicts. This log is the project's audit trail — the chain of custody for the requirements on the project. It is defensible to an owner, a lender, a federal contracting officer, or an auditor in any delivery context.

Cumulative chronological record reproduced in full from the workbook below. Entries 1–5 are the baseline document set; Entries 6–15 were processed during this cycle. The log is append-only — once a document is processed, its entry is preserved verbatim through every subsequent cycle.

## Cumulative Lineage — All 15 Entries

| # | Document | Type | Issued | Processed | Reqs + | Reg. After | Conflicts |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Northstar TJC Regulatory Requirements Summary v1.0 | Regulatory Summary | 2025-01-15 | 2025-01-28 | 22 | v1.0 | 0 |
| 2 | Heritage Owner Program Criteria Rev. 2 | Owner Program Req. | 2024-12-10 | 2025-01-28 | 24 | v1.0 | 0 |
| 3 | Heritage Health Campus Programming Document v1.0 | Owner Budget Auth. | 2024-12-01 | 2025-01-28 | 8 | v1.0 | 1 (CF-001) |
| 4 | Heritage Milestone Schedule v1.0 | Program Schedule | 2024-12-01 | 2025-01-28 | 6 | v1.0 | 0 |
| 5 | Northstar Clinic Equipment Schedule v1.0 | OFE Document | 2025-01-22 | 2025-01-28 | 10 | v1.0 | 2 (CF-002, CF-004) |
| 6 | Albuquerque/NM Commercial Building Code (2021 NMCBC) | Standard/Code | 2023-07-19 | 2025-01-28 | 10 | v1.1 | 0 |
| 7 | Heritage Health Campus A/E RFP HHC-2025-AE-001 v1.0 | RFP / Contract | 2025-04-15 | 2025-05-01 | 13 | v1.2 | 0 |
| 8 | A/E Design Services Kickoff Meeting Minutes | Meeting Minutes | 2025-05-14 | 2025-05-14 | 8 | v1.3 | 0 |
| 9 | NM CID/NM DOH AHJ Pre-Application Determination | AHJ Response | 2025-06-03 | 2025-06-03 | 5 | v1.4 | Resolves CF-005 |
| 10 | Geotechnical Consultant Report SGA-2025-0158 | Geotechnical Rpt. | 2025-06-06 | 2025-06-06 | 2 | v1.5 | 0 (unblocks VE-01) |
| 11 | Heritage Owner Written Design Directives HHC-ODD-001 | Owner Directive | 2025-06-13 | 2025-06-13 | 3 | v1.6 | Resolves CF-001, CF-002, CF-004 |
| 12 | AOR SD Outline Specifications HHC-SPEC-SD-001 | Specification | 2025-07-11 | 2025-07-11 | 3 | v1.7 | 0 |
| 13 | AOR 50% SD BIM Coordination Issues Log Rev 0.5 | BIM Issues Log | 2025-07-11 | 2025-07-11 | 4 | v1.8 | 2 NEW (CF-007, CF-008) |
| 14 | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 | CMAR Review | 2025-07-18 | 2025-07-18 | 4 | v1.9 | 0 (introduces 2 DP) |
| 15 | Cost Consultant 50% SD Cost Estimate | Cost Estimate | 2025-07-18 | 2025-07-18 | 2 | v2.0 | 0 |

Cycle 1 totals. 10 documents processed (Entries 6-15). 54 NEW records added (cumulative 124). 4 conflicts resolved (CF-001, CF-002, CF-004, CF-005). 2 NEW conflicts opened (CF-007, CF-008). Register version progression: v1.0 → v1.1 → v1.2 → v1.3 → v1.4 → v1.5 → v1.6 → v1.7 → v1.8 → v1.9 → v2.0. Sequential, append-only, no gaps.

# Section 8 — Next Cycle Dependencies

Forward-looking action orientation. Identifies anticipated submittals before next RIR cycle, input dependencies that block open DECISION-PENDING records, and the priority queue for the next processing cycle.

## Anticipated Submittals — Before RIR Cycle 2

Documents expected to enter the source-document pipeline before the next processing cycle. Each is flagged for early notification to Gallant so processing can begin promptly.

| Anticipated Submittal | Expected | Pipeline Action |
| --- | --- | --- |
| ICRA delivered (Northstar Infection Preventionist) | September 5, 2025 | Process as Source Document on receipt; closes GR-0019 and unblocks GR-0051 (sink placement). |
| CF-007 PT column structural directive (SER) | September 12, 2025 | Process as Owner Directive on receipt; closes CF-007 and updates GR-0116. |
| CF-008 MRI Zone IV duct + EES redesign (MEP-EOR) | September 26, 2025 | Process as Source Document on receipt (will be a 60% DD design directive); closes CF-008 and updates GR-0115, GR-0118. |
| AHU scope-allocation memo (CF-003 closure) | Before October 17, 2025 | Process as Owner Directive on receipt; closes CF-003. |
| Acoustic overlay scope-allocation memo (CF-006 closure) | Before October 17, 2025 | Process as Owner Directive on receipt; closes CF-006. |
| Elevator contractor engagement authorization | Within 7 days of report | Process as Owner Directive immediately; closes GR-0122. |
| Generator pad confirmation drawing | Within 14 days | Process as design submittal; closes GR-0121 and unblocks GR-0120 (gas permit). |
| 60% DD Basis of Design (AOR) | October 17, 2025 | Process as Source Document. Triggers RIR Cycle 2. |

## Input Dependencies — Owner / A/E / CMAR / AHJ

Eight inputs are blocking open DECISION-PENDING records or active conflicts. Listed in escalation priority.

| Input Required | Deadline | Records It Closes | Escalation Path |
| --- | --- | --- | --- |
| Elevator contractor engagement authorization | OVERDUE — Sep 1 | GR-0122 + unblocks construction-phase energize milestone | Tier 1 — Owner's PM issue written direction within 7 days. Cornerstone responds with vendor and contract structure within 14 days. |
| Generator pad confirmation | OVERDUE — Aug 15 | GR-0121 + unblocks GR-0120 gas permit chain | Tier 2 — Heritage + Cornerstone coordinate confirmation drawing. |
| CF-008 MRI Zone IV redesign directive | September 26, 2025 | CF-008 closes; GR-0115, GR-0118 → GOVERNING | Tier 1 — MEP Engineer of Record (MEP-EOR) issue design directive. |
| CF-007 PT column structural directive | September 12, 2025 | CF-007 closes; GR-0116 → GOVERNING | Tier 1 — Structural Engineer of Record (SER) evaluate alternatives, issue directive. |
| ICRA delivery | September 5, 2025 | GR-0019 + GR-0051 + unblocks HVAC zones | Northstar Infection Preventionist; Owner's Rep escalation if late. |
| Med gas additional locations (OAI-004) | Prior to 60% DD | GR-0038 | Northstar Clinical Director directive. |
| AHU scope-allocation memo (CF-003) | Before 60% DD | CF-003 closes; GR-0036 chain unblocks AHU procurement | Heritage + Northstar joint memo. |
| Acoustic overlay scope-allocation (CF-006) | Before 60% DD | CF-006 closes; GR-0050 cost allocation locks | Heritage + Northstar joint memo following 30% DD acoustic analysis. |

## Recommended Processing Sequence — Cycle 2

In sequence: process the elevator authorization and generator pad confirmation as soon as received (this resets the two overdue items); process CF-007 and CF-008 design directives in mid-September to unblock 60% DD coordination; process ICRA in early September to unblock HVAC zones; process scope-allocation memos for CF-003 and CF-006 before October 17; process the 60% DD Basis of Design on October 17 to formally trigger RIR Cycle 2.

Next Gate. 60% DD review on October 17, 2025. Three Tier 1 items must close. Two carryover conflicts (CF-003, CF-006) must close. Six baseline DECISION-PENDING items must close (mostly executable on procurement or design action, not further owner decisions). The next RIR is Cycle 2, produced upon receipt of the 60% DD Basis of Design.

# Section 9 — Cycle Comparison

Why this section exists. Section 9 shows what changed between the previous report and this one. It is the section that justifies the recurring engagement — each cycle, the owner sees what closed, what opened, what deadlines moved, and how the confidence indicator on the next gate shifted. This section appears for the first time in this report because there was no previous cycle to compare against in the Baseline.

## 9.1  Cycle Header

This is Cycle 1. It compares the project's state at baseline (January 28, 2025) to its state at 50 percent Schematic Design (July 18, 2025). 24.4 weeks elapsed between the two reports. Ten new source documents were processed during the cycle: the local building code adoption, the A/E Request for Proposals, the A/E kickoff meeting minutes, the AHJ's response on regulatory edition and occupancy, the geotechnical report, the owner's written design directives package, the SD outline specifications, the BIM coordination issues log, the CMAR constructability review, and the 50 percent SD cost estimate. The full lineage with dates and identifiers is in Section 7.

## 9.2  Closed Since Last Cycle

Fifteen open owner decisions closed and four conflicts resolved during this cycle. Each closure below cites the document that closed it and the closure memo Gallant issued at the time. Four closure memos went out during this cycle as part of Gallant's standard practice of documenting decision closures for the audit trail.

| Item | Resolution | Closure Document | Owner / DCM |
| --- | --- | --- | --- |
| GR-0018 | MRI vendor confirmed: Siemens MAGNETOM Altea 1.5T as design basis | D11 Owner Written Design Directives HHC-ODD-001 (June 13, 2025) | Biomedical Engineering Lead / DCM-HHC-001 |
| GR-0002 | MRI imaging service vendor locked (Siemens) — closes in chain with GR-0018 | D11 Owner Written Design Directives | Biomedical Engineering Lead / DCM-HHC-001 |
| GR-0033 | MRI room dimensions lock at 200 NSF per Siemens basis — closes in chain | D11 Owner Written Design Directives | Biomedical Engineering Lead / DCM-HHC-001 |
| GR-0039 | MRI structural point load locks at 7,700 lb per Siemens basis — closes in chain | D11 Owner Written Design Directives | Biomedical Engineering Lead / DCM-HHC-001 |
| GR-0021 | AHJ pre-application response received — FGI 2018 + NM amendments confirmed | D9 NM CID/NM DOH AHJ Pre-Application Determination NM-CID-HFS-2025-0603-MHC (June 3, 2025) | AOR Project Architect / DCM-HHC-002 |
| GR-0043 | FGI edition confirmed (2018) — closes in chain with GR-0021 | D9 AHJ Pre-Application Determination | AOR Project Architect / DCM-HHC-002 |
| GR-0044 | AHC occupancy classification confirmed by NM DOH — closes in chain | D9 AHJ Pre-Application Determination | AOR Project Architect / DCM-HHC-002 |
| GR-0035 | 8-ft AHC corridor widths lock per NM amendment — closes in chain | D9 AHJ Pre-Application Determination | AOR Project Architect / DCM-HHC-002 |
| GR-0029 | Generator scope allocated to Northstar TI ($220K upsize) | D11 Owner Written Design Directives HHC-ODD-001 | Owner's PM + Tenant Facilities Lead / DCM-HHC-003 |
| GR-0036 | AHU scope direction issued by Owner (interim) | D11 Owner Written Design Directives | Owner's PM + Tenant Facilities Lead / DCM-HHC-003 (partial) |
| GR-0020 | Geotechnical report received — Site Class C confirmed; VE-01 unlocked | D10 Geotechnical Consultant Geotechnical Report SGA-2025-0158 (June 6, 2025) | Owner's PM / DCM-HHC-004 |
| GR-0098 | PT LASER vendor confirmed (Summus Class IV) | D11 Owner Written Design Directives | Northstar Clinical / DCM-HHC-005 |
| GR-0099 | Traction table mounting confirmed (floor-mounted, no overhead track) | D11 Owner Written Design Directives | Northstar Clinical / DCM-HHC-005 |
| GR-0100 | Residential unit count confirmed at 145 units (no upward revision) | D11 Owner Written Design Directives | Owner's PM / DCM-HHC-006 |
| GR-0103 | ICRA on-file requirement confirmed at 90% CD per AHJ | D9 AHJ Pre-Application Determination | Northstar / DCM-HHC-002 (partial) |
| CF-001 | Generator capacity conflict resolved — 350 kW combined, allocated to Northstar | D11 Owner Written Design Directives | Resolves with GR-0029 / DCM-HHC-003 |
| CF-002 | MRI room area conflict resolved at 200 NSF Siemens basis | D11 Owner Written Design Directives | Resolves with GR-0018 / DCM-HHC-001 |
| CF-004 | MRI structural point load conflict resolved at 7,700 lb Siemens basis | D11 Owner Written Design Directives | Resolves with GR-0018 / DCM-HHC-001 |
| CF-005 | FGI edition authority conflict resolved — NM DOH on FGI 2018 + NM amendments | D9 AHJ Pre-Application Determination | Resolves with GR-0021 / DCM-HHC-002 |

## 9.3  Opened Since Last Cycle

Fifty-four new register records added. Two new conflicts opened. Two new DECISION-PENDING items entered at C1 close. Sorted by tier assignment — Tier 1 items first, then Tier 2, then Tier 3 grouped by source.

| Item | Description | Source Document | Tier / Rule |
| --- | --- | --- | --- |
| CF-008 | MRI Zone IV duct penetration + EES conduit routing — 2 distinct compliance failures | D13 AOR BIM Coordination Issues Log Rev 0.5 | Tier 1 (Rule 3 — active conflict, Critical) |
| CF-007 | PT open gym 14-inch column at Grid E-5 in column-free zone | D13 BIM Coordination Issues Log | Tier 1 (Rule 3 — active conflict, Critical) |
| GR-0122 | Elevator contractor engagement during SD (52-64 wk lead) | D14 CMAR Constructability Review | Tier 1 (Rule 4 — overdue + Rule 5 — irreversible critical-path) |
| GR-0121 | Generator pad location confirmation | D14 CMAR Constructability Review | Tier 2 (overdue, CMAR-introduced) |
| GR-0102 | NM DOH 90% CD plan review submission | D9 AHJ Pre-Application Determination | Tier 2 (Critical regulatory milestone) |
| GR-0119 | MRI delivery temporary opening in CD | D14 CMAR Constructability Review | Tier 3 (Critical, but fully scoped) |
| GR-0123 | TPC reconciliation tracking at 50% SD | D15 Cost Consultant Cost Estimate | Tier 3 (Critical, tracked) |
| GR-0124 | TI Allowance utilization tracking | D15 Cost Estimate | Tier 3 (Critical, tracked) |
| GR-0109 | MRI suite design basis: Siemens MAGNETOM Altea 1.5T | D11 Owner Written Design Directives | Tier 3 (Critical, GOVERNING from Day 1) |
| GR-0105 | 120 NSF exam room minimum (NM amendment NM-004) | D9 AHJ Pre-Application Determination | Tier 3 (Critical, regulatory) |
| GR-0106 | AHC occupancy NFPA 101 Ch. 20 egress | D9 AHJ Pre-Application Determination | Tier 3 (Critical, regulatory) |
| GR-0081 | Standard exam room 120 NSF (NMCBC amendment) | D6 Albuquerque/NM Commercial Building Code | Tier 3 (Critical, regulatory) |
| GR-0071–0080 | 10 records — NM Commercial Building Code framework | D6 NMCBC | Tier 3 (group — High to Low impact) |
| GR-0082–0093 | 12 records — A/E procurement and deliverables structure | D7 A/E RFP | Tier 3 (group — High to Low impact) |
| GR-0094–0097 | 4 records — Kickoff Meeting program changes | D8 A/E Kickoff Minutes | Tier 3 (group) |
| GR-0107–0108 | 2 records — Geotechnical foundation and seismic basis | D10 Geotechnical Report | Tier 3 |
| GR-0110–0114 | 5 records — Owner Directives implementation detail | D11 Owner Directives | Tier 3 |
| GR-0115–0118 | 4 records — SD BIM coordination items (CF-007, CF-008 included) | D13 BIM Issues Log | Tier 1 / Tier 3 mixed |
| GR-0119–0122 | 4 records — CMAR constructability findings | D14 CMAR Review | Tier 1 / Tier 2 / Tier 3 |

## 9.4  Status Migration Summary

Five-question summary of how the project's overall standing changed from the previous report to this one.

### Q1.  Net change in open decisions

Opening (baseline): 16 open. Closed this cycle: 15. Opened this cycle: 2. Ending: 8 open (6 not overdue + 2 overdue at C1 close). The trend is favorable — the design team and owner cleared all 14 baseline upstream gate-blockers (MRI vendor, AHJ, geotech, generator, AHU direction, PT equipment, residential unit count, ICRA confirmation requirement). The 2 new items at C1 close are CMAR-introduced and were not foreseeable from the source documents available at baseline. Net change: −8 open items (50% reduction).

### Q2.  Net change in open conflicts

Opening (baseline): 6 open. Closed this cycle: 4 (CF-001, CF-002, CF-004, CF-005). Opened this cycle: 2 (CF-007, CF-008). Ending: 4 open. Three of the four resolutions occurred in chain with the MRI vendor selection and AHJ response — exactly the cascade Section 8 of the Baseline RIR predicted. The two new conflicts came from the BIM coordination process at 50% SD, which is the design phase where this category of conflict is expected to surface. Net change: −2 open conflicts (33% reduction).

### Q3.  Deadlines that moved

| Item | Original Deadline | New Deadline | Reason |
| --- | --- | --- | --- |
| GR-0019 (ICRA) | June 27, 2025 | September 5, 2025 | Northstar Infection Preventionist requested extension to align with finalized HVAC zone design |
| GR-0023 (RF shielding) | October 31, 2025 | October 31, 2025 (after MRI vendor confirmation, June 13) | No change in deadline; upstream blocker (MRI vendor) closed earlier than required, accelerating spec finalization |
| GR-0022 (Generator procurement) | October 31, 2025 | October 31, 2025 | No change; allocation now resolved (D11), procurement now executable |

### Q4.  How the confidence indicator changed

Baseline cycle: AMBER (16 open decisions including 2 overdue at the start of design). Current cycle: AMBER (cleared 15 of 16 baseline items, but 2 new gate-blocking conflicts surfaced from the BIM coordination run and 2 new overdue procurement items entered from the CMAR review). The indicator did not improve from baseline despite strong closure performance — the new conflicts and the elevator engagement decision are the reason. The team has demonstrated capacity to clear gate-blockers, but the 8-week window to the next gate is tighter than the prior cycle's 24-week window.

### Q5.  What this cycle's pace tells us about the next gate

Resolution rate this cycle was strong — 15 of 16 baseline items closed in 24 weeks, an average of one closure every 11 days. The team has demonstrated capacity to clear gate-blocking decisions at well above the rate required to clear the current 8 open items in the 13 weeks remaining to the next gate. The 60 percent Design Development gate on October 17, 2025 is achievable if (a) the two new BIM-driven conflicts route to resolution paths within the next two weeks, (b) the elevator engagement decision is authorized within 7 days of this report, and (c) the two remaining carryover conflicts close before mid-October.

A note on methodology improvement. Gallant's methodology evolved between the Baseline report and this Cycle 1 report. The Baseline used the methodology in force at project initiation; this report uses the updated methodology. The visible changes for the reader: the executive summary now follows a structured four-part format engineered for forwarding to a project sponsor, and this Cycle Comparison section (Section 9) is new — it didn't exist in the Baseline format. Methodology improvements are surfaced to clients explicitly so the changes between cycles are visible, never hidden.

# Appendix A — Workbook Integrity Findings

Why this appendix exists. Gallant runs an internal workbook-integrity check on each report before it leaves the office. The findings below illustrate Gallant's commitment to surfacing its own workbook issues with the same rigor applied to the project record. This is a feature of the methodology, not a defect — clients receive this kind of transparency in the reports they receive. The single finding below is a Gallant-internal workbook template item; it does not affect the audit-trail integrity of the closures documented in Section 9.

This appendix documents one workbook template item Gallant flagged for itself before producing the next cycle report.

## Gate 2 Validation Result

| Field | Result |
| --- | --- |
| Tests passed | 9 of 10 |
| T6 status (gating) | PASS — lineage continuity intact, 15 entries sequential, all fields populated |
| T8 status (disclosure) | PASS — Critical at 25.0%, under 30% ceiling |
| Disposition | Hard fail on T10 — DecisionResolutionMemo column not present in Decision_Register sheet structure. Workbook proceeded to RIR generation under analyst judgment because the closure audit trail is intact through alternate channel (Decision_Register Status column carries 'Resolved — see register notes' for closed items, with full closure detail in the Decision Closure Memos referenced in Section 9). T10 column gap is a workbook-template enhancement, not an audit-trail breach. |

## WBI-001 — Decision_Register lacks DecisionResolutionMemo column

| Field | Specification |
| --- | --- |
| Severity | High (workbook integrity) |
| Found in | Gallant_Requirements_Workbook_Heritage_v2_0.xlsx — Decision_Register sheet |
| Finding | The Decision_Register sheet does not include a DecisionResolutionMemo column referencing the DCM-HHC-NNN identifier for each closed item. Per Doc 5 v1.4 Decision Closure Workflow Step 2, every resolved DECISION-PENDING record should populate this field at closure. The column is required for Gate 2 Test T10 (Decision Closure Memo audit trail) to evaluate cleanly on Cycle 2 and beyond. |
| Expected per methodology | Decision_Register columns per Doc 5 v1.4 should include: Req ID · Requirement (Short) · DecisionType · Trigger Language · What Must Happen to Close · DecisionOwner · DecisionDeadline · DecisionStatus · DecisionResolutionDate · DecisionResolutionMemo. The last two are missing in the current workbook structure. |
| Cycle 1 audit-trail intactness | All 15 baseline closures during this cycle are documented in Section 9 with explicit DCM identifiers (DCM-HHC-001 through DCM-HHC-006). The closure trail is intact for Cycle 1 — the workbook structure deficiency does not break the audit trail, but it is the same class of finding as DEV-001 and DEV-002 from the Baseline RIR Appendix A. |
| Recommended correction | Add DecisionResolutionDate and DecisionResolutionMemo columns to the Decision_Register sheet template before Cycle 2 RIR generation. Backfill the 15 closures from this cycle with their corresponding DCM identifiers. Update workbook template in Doc 4 v1.3 Template attachment if applicable. |
| Correction owner | Gallant Project Solutions (internal workbook template) |
| Target close | Before Cycle 2 RIR generation (target: October 17, 2025) |

## Reconciliation to Baseline Appendix A Deviations

The Baseline RIR Appendix A documented 10 deviations. Seven have closed during this cycle. Status update:

| DEV | Description | Status | Closure Detail |
| --- | --- | --- | --- |
| DEV-001 | Decision_Register header inconsistent with body count | CLOSED | Workbook structure corrected; T2 PASS this cycle |
| DEV-002 | DecisionType field carrying RiskDriver tags | CLOSED | Reclassification complete; T3 PASS this cycle |
| DEV-003 | Equipment Schedule lists two MRI vendors as concurrent basis | CLOSED | D11 Owner Directive confirmed Siemens basis |
| DEV-004 | NNN Lease Exhibit D silent on AHU + generator scope | PARTIAL | Generator scope closed via D11. AHU scope still open as CF-003. |
| DEV-005 | FGI edition adoption unconfirmed | CLOSED | D9 AHJ response confirmed FGI 2018 + NM amendments |
| DEV-006 | Geotechnical Report overdue | CLOSED | D10 Geotechnical Report received June 6, 2025 |
| DEV-007 | AHJ pre-application overdue | CLOSED | Pre-application submitted; D9 response received June 3, 2025 |
| DEV-008 | ICRA delivery undertracked | OPEN | ICRA still pending — now elevated to Section 4 Tier 2 with Sep 5 deadline |
| DEV-009 | TPC variance exceeds BCR-004 trigger | CLOSED | D15 50% SD cost estimate brought variance to 4.4% — below threshold |
| DEV-010 | Verification_Matrix lacks dependency-blocker linkage | OPEN | Methodology enhancement deferred to next workbook template revision |

Cycle 1 deviation closeout. Of the 10 baseline deviations, 7 closed during this cycle, 1 partially closed (DEV-004 generator portion only), and 2 remain open as forward-looking items (DEV-008 ICRA delivery is now Section 4 Tier 2; DEV-010 Verification_Matrix enhancement carries forward as a workbook template item alongside WBI-001).

End of Report

Requirements Intelligence Report™ — Cycle 1 (50% SD Baseline)

Heritage Health Campus — Northstar Ambulatory Care Clinic    ·    Run ID HHC-REG-010    ·    Register v2.0    ·    July 18, 2025

Prepared by

GALLANT PROJECT SOLUTIONS LLC

Greg Tuite, PE PMP — Principal

Service-Disabled Veteran-Owned Small Business (SDVOSB)   ·   Veteran-Owned Small Business (VOSB)   ·   SBA Registered

© 2026 Gallant Project Solutions LLC. PROPRIETARY AND CONFIDENTIAL. All rights reserved.