## Summary
GALLANT PROJECT SOLUTIONS LLC · HERITAGE HEALTH CAMPUS · REQUIREMENTS REGISTER v2.0
Methodology: Doc 5 v1.4 / Doc 4 v1.3 · SD Baseline · Documents D1–D15 Processed · Gate 2 CLEARED
Metric | Value | Notes
Register Version | v2.0 | SD Baseline — D1–D15 processed
Run ID | HHC-REG-010 | SD Baseline run under Doc 5 v1.4
Run Type | SD Baseline — Documents 1–15
Total Requirements | 124 | GR-0001 through GR-0124
GOVERNING (Active) | 113 | Active, verified requirements
DECISION-PENDING | 8 | Owner action required — 3 overdue
CONFLICT-PENDING | 3 | CF-007, CF-008 active
SUPERSEDED | 0
Active Conflicts | 4 OPEN / 4 RESOLVED | CF-003, CF-006, CF-007, CF-008 open
Documents Processed | 15 | D1–D15
Docs Processed List | D1: TJC Reg D2: OPC Rev.2 D3: Programming D4: Schedule D5: Equipment D6: ABQ/NMCBC D7: A/E RFP D8: Kickoff Minutes D9: AHJ Pre-App D10: Geotech D11: Owner Directives D12: SD Outline Specs D13: BIM Issues Log D14: CMAR Review D15: Cost Estimate
Gate 2 Status | CLEARED — 9/10 PASS · 1 N/A | RIR generation authorized
Next Version | v2.1 | After RIR Cycle 1 generation
Project | Heritage Health Campus | Northstar Ambulatory Care Clinic
Analyst | Greg Tuite, PE PMP | Gallant Project Solutions LLC
SDVOSB / VOSB | Certified | SBA-certified Service-Disabled Veteran-Owned Small Business
Proprietary Notice | © 2026 Gallant Project Solutions LLC | All rights reserved — Requirements Intelligence Report™

## Requirements_Register
HERITAGE HEALTH CAMPUS · GALLANT REQUIREMENTS REGISTER v2.0 · SD BASELINE · 124 REQUIREMENTS · © 2026 GALLANT PROJECT SOLUTIONS LLC · SDVOSB/VOSB
RequirementID | RequirementUID | ParentRequirementID | HierarchyLevel1 | HierarchyLevel2 | HierarchyLevel3 | RequirementType | RequirementCategory | RequirementStatement | RequirementSubject | RequirementIntent | GoverningParameter | NumericConstraint | Condition | ExceptionOrQualifier | SourceType | SourceDocument | SourceSection | VerificationMethod | VerificationAuthority | Applicability | ResponsibleDiscipline | ResponsibleStakeholder | ScopeResponsibility | DesignDriver | RequirementStatus | ChangeImpactLevel | ImpactDomains | ContractTraceability | Confidence | Notes | CriticalityScore | CriticalityCategory | RiskDrivers | KeywordFlags | DecisionFlag | DecisionType | TriggerLanguage | DecisionOwner | DecisionDeadline | DecisionStatus | ConflictRefs | DecisionResolutionMemo
GR-0001 | HHC-FR-001 | — | Functional Requirements | Clinical Services | Primary Care | Functional | Clinical — Primary Care | The clinic shall provide primary care services supporting a minimum of 60 scheduled patient encounters per operating day across 16 exam rooms. | Primary Care Clinic | Operational capacity | Patient throughput capacity | 60 encounters/day minimum | During scheduled operating hours | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §1.1 Clinic Services | Test | Northstar Clinical Operations — throughput simulation at 60% DD | Floors 1–2, Northstar clinical TI | Architecture | Northstar Health System | TI scope — Northstar | Exam room count drives floor plan and NSF allocation | GOVERNING | High | Architecture / MEP / IT | NNN Lease — TI scope | High | 16 exam rooms required per program | 82 | High | DECISION_REQUIRED | 60 encounters | shall | TJC accreditation |  |  |  | N/A
GR-0002 | HHC-FR-002 | — | Functional Requirements | Clinical Services | Medical Imaging | Functional | Clinical — Imaging | The clinic shall provide medical imaging services including one Class 1 diagnostic radiography room and one Class 2 MRI room, 1.5T closed-bore, model TBD per OAI-001. | Imaging Suite | Service provision | Imaging modality configuration | 1 X-ray Class 1 + 1 MRI Class 2 (1.5T) | All operating hours | Vendor TBD | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §1.1 / §B Imaging Suite | Inspection | Northstar Biomedical Engineering — equipment installation verified | Floors 1–2, Imaging Suite | Architecture / Structural | Northstar Health System | TI scope — Northstar | MRI room structural, RF shielding, and zone design | GOVERNING | Critical | Architecture / Structural / Electrical / MEP | NNN Lease — TI scope | Medium | OAI-001: MRI vendor under active evaluation — Siemens vs. GE. Structural point load, equipment room size, and RF shielding spec all vendor-dependent. ¦ CLOSED by D11: Siemens MAGNETOM Altea 1.5T confirmed per HHC-ODD-001 Directive 1. GE option eliminated. Design basis locked. | 95 | Critical | DECISION_REQUIRED ¦ LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION | model TBD | N | TBD-UNRESOLVED | model TBD — MRI vendor under active evaluation | Northstar Biomedical Engineering — Biomedical Engineering Lead | June 13, 2025 | Resolved
GR-0003 | HHC-FR-003 | — | Functional Requirements | Clinical Services | Physical Therapy | Functional | Clinical — Physical Therapy | The clinic shall provide physical therapy services in a dedicated suite containing minimum 4 open gym treatment stations, 2 private treatment rooms, and one hydrotherapy area with whirlpool. | Physical Therapy Suite | Service provision | PT service program | 4 open stations + 2 private rooms + 1 hydrotherapy | All PT operating hours | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §1.1 / §C Physical Therapy Suite | Inspection | Northstar Clinical Operations — space program verification | Floors 1–2, PT Suite | Architecture | Northstar Health System | TI scope — Northstar | PT equipment layout drives structural floor load and MEP rough-in | GOVERNING | Moderate | Architecture / Structural / MEP | NNN Lease — TI scope | High | OAI-005: PT equipment plan not yet provided. LASER unit and traction table added post-equipment-schedule. | 71 | High | DECISION_REQUIRED | shall provide | shall | PT equipment plan | Northstar Clinical Operations | June 13, 2025 | Open | N/A
GR-0004 | HHC-FR-004 | — | Functional Requirements | Accreditation | TJC AHC | Functional | Regulatory — Accreditation | The clinic shall achieve Joint Commission Ambulatory Health Care (TJC AHC) accreditation on Day 1 of operations. | Clinic Operations | Accreditation compliance | TJC AHC program compliance | Day 1 accreditation | At initial occupancy and operations | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §1 / OPC Overview | Demonstration | TJC AHC accreditation survey result | Floors 1–2, Northstar clinical TI | All disciplines | Northstar Health System — Compliance | TI scope — all clinical | Governs 52 RCR requirements across all disciplines | GOVERNING | Critical | Architecture / MEP / IT / Operations | NNN Lease — operational commencement | High | All RCR requirements in this register trace to TJC AHC accreditation as the top-level compliance framework. | 90 | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY | shall achieve | shall comply | accreditation | — | — | — | N/A
GR-0005 | HHC-FR-005 | — | Functional Requirements | Patient Flow | Reception | Functional | Architecture — Patient Flow | Primary care patient reception shall have direct, unobstructed visual sightlines to the patient waiting area. No intervening walls, blind corners, or visual barriers are permitted. | Reception Workstation | Safety — workplace violence prevention | Visual sightline from reception to waiting | Unobstructed direct visual access | At all times during clinic operations | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §3.1 Patient Flow and Adjacency | Inspection | Architect of Record (AOR) — SD floor plan review and field verification | Primary Care Suite, Floor 1 | Architecture | Northstar Clinical Operations | TI scope — Northstar | Floor plan layout | GOVERNING | Moderate | Architecture | NNN Lease — TI scope | High | Direct safety requirement. Relates to SLR-001 access control and TJC RQ-024 workplace violence prevention. | 55 | Moderate | LIFE_SAFETY | shall | unobstructed | visual sightline | — | — | — | N/A
GR-0006 | HHC-FR-006 | — | Functional Requirements | Patient Waiting | Zones | Functional | Architecture — Patient Accommodation | Patient waiting shall be provided in two separate designated zones: primary care waiting (minimum 20 seats) and imaging waiting (minimum 10 seats). Zones shall not be combined. | Patient Waiting Areas | Operational functionality | Patient waiting capacity and zone separation | 20 seats PC / 10 seats imaging minimum | During all operating hours | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §A Primary Care Suite / §B Imaging Suite | Inspection | Architect of Record (AOR) — seat count and zone separation at SD | Floors 1–2, Northstar clinical TI | Architecture | Northstar Clinical Operations | TI scope — Northstar | Waiting zone separation affects floor plan layout on both floors | GOVERNING | Moderate | Architecture | NNN Lease — TI scope | High | Two zones required; combined zone is not acceptable. | 48 | Moderate | LIFE_SAFETY | 20 seats / 10 seats | shall not be combined | zone separation | — | — | — | N/A
GR-0007 | HHC-FR-007 | GR-0003 | Functional Requirements | Clinical Services | Telemedicine | Functional | Clinical — Technology | The clinic shall include two dedicated telemedicine rooms with integrated AV equipment, high-bandwidth data, and acoustic treatment achieving minimum absorption coefficient 0.20 (250–2000 Hz). | Telemedicine Rooms | Service provision — telehealth | Telemedicine room program and acoustic standard | 2 rooms + absorption coefficient ≥ 0.20 | During clinic operations | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-018 / TJC AHC | Test | Acoustic subconsultant — field measurement at commissioning | Floors 1–2, Telemedicine Rooms | Architecture / Acoustic | Northstar Clinical Operations | TI scope — Northstar | Acoustic treatment and AV infrastructure rough-in | GOVERNING | Moderate | Architecture / IT / Acoustic | NNN Lease — TI scope | High | AV equipment is OFE by Northstar. Infrastructure (conduit, power, data) in TI scope. | 52 | Moderate | MULTI_DISCIPLINE_COORDINATION | 0.20 absorption coefficient | shall | acoustic standard | — | — | — | N/A
GR-0008 | HHC-FR-008 | — | Functional Requirements | HIPAA Compliance | Acoustic Privacy | Functional | Architecture — HIPAA | All clinical spaces shall prevent inadvertent disclosure of PHI through acoustic means. Conversations in exam rooms shall not be clearly intelligible in adjacent exam rooms, corridors, or waiting areas. | Clinical Spaces — All | HIPAA compliance | Acoustic privacy across all clinical spaces | PHI not intelligible through partitions | During all patient encounters | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §3.2 Privacy and Acoustic Requirements | Test | Acoustic subconsultant — field measurement at commissioning | Floors 1–2, all clinical spaces | Architecture / Acoustic | Northstar Health System — Compliance | TI scope — Northstar | Partition STC ratings throughout clinical TI | GOVERNING | High | Architecture / Acoustic | NNN Lease — TI scope | High | HIPAA is a federal regulatory requirement. Reinforces TJC RQ-017 acoustic isolation standard. | 75 | High | REGULATORY_APPROVAL ¦ LIFE_SAFETY | shall not be clearly intelligible | shall prevent | PHI disclosure | — | — | — | N/A
GR-0009 | HHC-PR-001 | — | Performance Requirements | Lighting | Clinical Task | Performance | Electrical — Lighting | Task lighting in all exam rooms, procedure rooms, and treatment rooms shall provide a minimum of 50 footcandles at work surface height. Exam rooms shall include tunable white LED (3000K–5000K). | Clinical Exam and Treatment Rooms | Performance — lighting quality | Task illuminance level | 50 fc minimum at work surface + tunable white LED | At all clinical task surfaces during operations | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.3 Electrical / IES Healthcare Lighting | Test | MEP Engineer of Record (MEP-EOR) (Electrical) — illuminance measurement at commissioning | All exam rooms, treatment rooms, procedure rooms | Electrical | Northstar Health System | TI scope — Northstar | Lighting fixture type and layout | GOVERNING | Moderate | Electrical / Architecture | NNN Lease — TI scope | High | 50 fc is IES healthcare standard. Tunable white enables clinical assessment at appropriate CCT. | 55 | Moderate | MULTI_DISCIPLINE_COORDINATION | 50 footcandles minimum | shall provide | at work surface height | — | — | — | N/A
GR-0010 | HHC-PR-002 | — | Performance Requirements | HVAC | Clinical Ventilation | Performance | Mechanical — HVAC | Clinical exam rooms shall achieve minimum 6 total air changes per hour (ACH) with minimum 2 outdoor air ACH. No recirculation to adjacent clinical zones. | Exam Rooms — HVAC | Performance — indoor air quality | Ventilation rate and outdoor air fraction | 6 total ACH / 2 OA ACH minimum | During clinic operating hours | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-009 / ASHRAE 170 Table 7.1 | Test | MEP Engineer of Record (MEP-EOR) — TAB report at commissioning | All exam rooms, clinical zones | Mechanical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | HVAC system sizing and VAV terminal unit design | GOVERNING | High | Mechanical / Architecture | NNN Lease — TI scope | High | ASHRAE 170 compliance is a TJC AHC accreditation requirement per RQ-009. | 78 | High | REGULATORY_APPROVAL ¦ LIFE_SAFETY | 6 ACH / 2 OA ACH | shall achieve | during operating hours | — | — | — | N/A
GR-0011 | HHC-PR-003 | GR-0010 | Performance Requirements | HVAC | Isolation Room | Performance | Mechanical — HVAC Isolation | Isolation room shall achieve minimum 12 total ACH with minimum 2 OA ACH, maintained negative pressure relative to adjacent corridor. Pressure differential monitored continuously with audible alarm. | Isolation Room | Performance — infection control | Isolation room ventilation and pressure relationship | 12 ACH minimum / negative pressure / continuous monitoring | At all times when isolation room is in service | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-008 / ASHRAE 170 / FGI 2022 §2.1-3.6 | Test | MEP Engineer of Record (MEP-EOR) — TAB + pressure differential test at commissioning | Isolation Room, Floor 1 | Mechanical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | Dedicated exhaust fan with no recirculation; continuous monitoring device | GOVERNING | Critical | Mechanical / Controls | NNN Lease — TI scope | High | Life safety and infection control. Negative pressure failure = patient and staff safety risk. | 92 | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | 12 ACH / negative pressure | shall achieve | at all times | — | — | — | N/A
GR-0012 | HHC-PR-004 | — | Performance Requirements | HVAC | MRI Environment | Performance | Mechanical — MRI HVAC | MRI magnet room temperature shall be maintained 65–72°F year-round with RH 30–60% year-round. MRI equipment room shall be maintained 65–75°F year-round with 24/7 dedicated cooling. | MRI Magnet Room / Equipment Room | Performance — MRI operational environment | Temperature and humidity control | 65–72°F / RH 30–60% (magnet room); 65–75°F 24/7 (equipment room) | Year-round, 24/7 | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-020 / EQ-021 Equipment Schedule | Test | MEP Engineer of Record (MEP-EOR) — 30-day trending post-commissioning | MRI Magnet Room + Equipment Room | Mechanical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | Dedicated precision cooling unit 24/7; non-ferrous components in magnet field | GOVERNING | High | Mechanical / Structural / Electrical | NNN Lease — TI scope | High | 24/7 cooling failure = MRI shutdown. Critical for equipment protection and patient scheduling. | 88 | High | LIFE_SAFETY ¦ LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION | 65–72°F / 30–60% RH | shall be maintained | year-round 24/7 | — | — | — | N/A
GR-0013 | HHC-PR-005 | — | Performance Requirements | Plumbing | Hot Water | Performance | Plumbing — Domestic Hot Water | Domestic hot water shall be maintained at minimum 110°F at the point of use at all clinical handwashing stations. Thermostatic mixing valves (ASSE 1070) shall be provided at all clinical fixtures. | Domestic Hot Water System | Performance — infection prevention | Hot water temperature | 110°F minimum at point of use | At all clinical handwashing stations during operating hours | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.3 Plumbing | Test | MEP Engineer of Record (MEP-EOR) — temperature measurement at commissioning | All clinical handwashing stations, Floors 1–2 | Plumbing | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | Separate clinical domestic water riser with hot water recirculation loop | GOVERNING | High | Plumbing / Mechanical | NNN Lease — TI scope | High | Legionella prevention. ASSE 1070 valves required at point of use to prevent scalding while maintaining hot water temperature in distribution system. | 72 | High | REGULATORY_APPROVAL ¦ LIFE_SAFETY | 110°F minimum | shall be maintained | at all clinical fixtures | — | — | — | N/A
GR-0014 | HHC-PR-006 | — | Performance Requirements | Electrical | UPS Runtime | Performance | Electrical — Power Continuity | UPS backup power for PACS workstations and IT/server room shall provide minimum 30-minute runtime at full design load. | UPS System — PACS / IT | Performance — power continuity | UPS runtime | 30-minute minimum at full design load | During utility power interruption | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.2 Electrical | Test | MEP Engineer of Record (MEP-EOR) — UPS runtime test at commissioning | IT Server Room | Electrical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | UPS system (EQ-061, OFE by Northstar) + 208V/60A 3-phase circuit in TI scope | GOVERNING | Moderate | Electrical / IT | NNN Lease — TI scope | High | 30-minute runtime protects in-flight PACS studies during power interruption. OFE by Northstar. | 55 | Moderate | HIGH_COST_INFRASTRUCTURE | 30-minute runtime | shall provide | at full design load | — | — | — | N/A
GR-0015 | HHC-PR-007 | GR-0003 | Performance Requirements | Structural | PT Hydrotherapy | Performance | Structural / MEP — PT | PT hydrotherapy whirlpool area shall have dedicated 200A electrical service, waterproof floor-to-ceiling tile, and floor drain within 12 inches of whirlpool unit. | PT Hydrotherapy Area | Performance — equipment infrastructure | PT hydrotherapy electrical and waterproofing | 200A electrical + waterproof finishes + floor drain ≤12" from unit | During PT operations | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-046 Equipment Schedule | Inspection | AOR / MEP-EOR — field verification at substantial completion | PT Hydrotherapy Area | Electrical / Architecture | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | 200A feeder; waterproof membrane; tile to ceiling; floor drain | GOVERNING | High | Structural / Electrical / Architecture / Plumbing | NNN Lease — TI scope | High | Whirlpool unit weight 900 lbs full. Structural slab must be rated for 150 psf + water load. Waterproof membrane required under all tile. | 68 | High | HIGH_COST_INFRASTRUCTURE ¦ MULTI_DISCIPLINE_COORDINATION | 200A / waterproof / drain ≤12" | shall have | PT hydrotherapy | — | — | — | N/A
GR-0016 | HHC-PR-008 | GR-0008 | Performance Requirements | Acoustic | Exam Room Isolation | Performance | Acoustic — Partition | Acoustic separation between exam rooms sharing a common wall shall achieve minimum STC 45. Acoustic separation between exam rooms and adjacent corridors or waiting areas shall achieve minimum STC 45. | Exam Room Partitions | Performance — HIPAA acoustic privacy | STC rating for exam room partitions | STC 45 minimum | Between adjacent exam rooms and adjacent corridors/waiting | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-017 / FGI 2022 Table 1-7A | Analysis + Test | Acoustic subconsultant — calculation at DD + field measurement at commissioning | All exam room partitions, Floors 1–2 | Architecture / Acoustic | Acoustic Subconsultant | TI scope — Northstar | Partition assembly specification in architectural CDs | GOVERNING | High | Architecture / Acoustic | NNN Lease — TI scope | High | HIPAA and TJC accreditation requirement. See also GR-0008 (HIPAA FR) and RCR-015 (STC 60 clinical/residential). | 72 | High | REGULATORY_APPROVAL | STC 45 minimum | shall achieve | between adjacent exam rooms | — | — | — | N/A
GR-0017 | HHC-SMR-001 | — | Schedule & Milestone Requirements | Pre-Design | Program Issuance | Schedule | Program Governance | Owner Program Criteria Rev. 2 shall be issued and accepted as the governing clinical program document prior to Schematic Design initiation. | Owner Program Criteria | Program governance — schedule sequencing | Program document issuance | Issued prior to SD initiation | Before SD NTP | None | ProgramDoc | Heritage Health Campus Programming Document v1.0 | §D Milestone Schedule / Programming Doc | Inspection | Gallant / Owner — document in project record dated Dec 10, 2024 | Pre-SD, pre-design phase | Program Management | Gallant Project Solutions LLC | Owner scope | Program governs all subsequent design and extraction | GOVERNING | Low | Program Management | N/A | High | COMPLETE — OPC Rev. 2 issued December 10, 2024. | 20 | Low | — | prior to SD initiation | shall be issued | before SD NTP | — | — | — | N/A
GR-0018 | HHC-SMR-002 | — | Schedule & Milestone Requirements | Pre-SD | MRI Model Decision | Schedule | Procurement — Long Lead | MRI model and vendor shall be confirmed in writing by Northstar Biomedical Engineering no later than June 13, 2025, before 50% SD submittal. | MRI Equipment — Vendor Selection | Schedule sequencing — design dependency | MRI model confirmation deadline | June 13, 2025 | Prior to 50% SD structural framing | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-020 Equipment Schedule | Inspection | Gallant — written vendor confirmation in project record | Pre-SD gate | Program Management | Northstar Biomedical Engineering | Owner scope (OFE) | MRI vendor confirmation unblocks structural, floor plan, and RF shielding design | GOVERNING | Critical | Structural / Architecture / MEP / Electrical | NNN Lease — OFE | Medium | Gate blocker. Siemens vs. GE under active evaluation. Structural point load: Siemens 7,700 lb vs. GE 8,100 lb. Equipment room: 200 NSF (Siemens) vs. 240 NSF (GE). CONFLICT-C002 active. ¦ CLOSED by D11: MRI vendor confirmed — Siemens MAGNETOM Altea 1.5T. SMR-002 CLOSED. | 95 | Critical | DECISION_REQUIRED ¦ LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION | model TBD | N | TBD-UNRESOLVED | model TBD — vendor under active evaluation | Northstar Biomedical Engineering — Biomedical Engineering Lead | June 13, 2025 | Resolved
GR-0019 | HHC-SMR-003 | — | Schedule & Milestone Requirements | Pre-SD | ICRA Delivery | Schedule | Infection Control — Schedule | ICRA shall be completed by Northstar infection preventionist and transmitted to A/E no later than June 27, 2025, before 50% SD submittal. | ICRA — Infection Control Risk Assessment | Schedule sequencing — HVAC design dependency | ICRA completion deadline | June 27, 2025 | Prior to HVAC zone boundary finalization | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-020 / FGI 2022 ICRA | Inspection | Gallant — ICRA document in project record with A/E receipt confirmation | Pre-SD gate | Mechanical / Program Management | Northstar Infection Preventionist | Owner scope | ICRA governs HVAC zone boundaries, negative pressure extents, and sink placement | DECISION-PENDING | Critical | Mechanical / Architecture | NNN Lease — Owner obligation | Medium | Gate blocker. ICRA not received. HVAC zone boundaries cannot be finalized without ICRA. TJC accreditation requires ICRA at programming stage. | 90 | Critical | DECISION_REQUIRED ¦ REGULATORY_APPROVAL | not yet completed | Y | TBD-UNRESOLVED | not yet completed | Northstar — Infection Preventionist | June 27, 2025 | Open
GR-0020 | HHC-SMR-004 | — | Schedule & Milestone Requirements | Pre-SD | Geotechnical Report | Schedule | Structural — Schedule Dependency | Geotechnical investigation report shall be received from Geotechnical Consultant prior to 50% SD structural narrative development. | Geotechnical Report | Schedule sequencing — structural design dependency | Geotech report receipt | Prior to 50% SD structural narrative | Before foundation design is finalized | None | ProgramDoc | Heritage Health Campus Milestone Schedule v1.0 | MS-023 Milestone Schedule | Inspection | Gallant / SER — report in project record; structural narrative references confirmed Site Class | Pre-50% SD | Structural | Heritage Development Partners | Heritage scope (separate contract) | Foundation system and VE-01 evaluation both blocked pending report | GOVERNING | High | Structural / Cost | Heritage separate contract | Medium | OVERDUE. Report authorized December 2024. Not yet received. Site Class D assumed. VE-01 ($180K–$340K foundation savings) unavailable until report received. ¦ CLOSED by D10: Geotech report SGA-2025-0158 received June 6, 2025. Site Class C confirmed. OVERDUE status cleared. VE-01 activated. | 78 | High | DECISION_REQUIRED ¦ SCOPE_GAP | not yet received | N | TBD-UNRESOLVED | not yet received | Heritage Development Partners — Owner's PM | OVERDUE — June 6, 2025 | Resolved
GR-0021 | HHC-SMR-005 | — | Schedule & Milestone Requirements | Pre-SD | AHJ Pre-Application | Schedule | Regulatory — AHJ Confirmation | AHJ pre-application inquiry to NM DOH confirming applicable FGI edition and AHC occupancy classification shall be submitted no later than May 23, 2025. | AHJ Pre-Application — NM DOH | Regulatory — schedule sequencing | AHJ FGI edition and occupancy confirmation | Submitted May 23, 2025 | Before SD corridor widths and egress design are finalized | None | ProgramDoc | Heritage Health Campus Milestone Schedule v1.0 | MS-020 Milestone Schedule | Inspection | Gallant — pre-application and AHJ response in project record | Pre-SD gate | Architecture / Regulatory | Architect of Record (AOR) | A/E scope | AHC occupancy and FGI edition govern 8 ft corridor widths, egress, and imaging room classifications | GOVERNING | Critical | Architecture / Regulatory | A/E Contract — Exhibit A scope | Medium | DF-NEW-001 active: NM DOH on FGI 2018, not 2022. AHC occupancy unconfirmed. 8 ft corridor width requirement conditional on AHC confirmation. ¦ CLOSED by D9: AHJ pre-application response received June 3, 2025. SMR-005 CLOSED. ¦ CLOSED by D9: AHJ pre-application response received June 3, 2025. SMR-005 CLOSED. | 88 | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | FGI edition confirmation pending | N | CONDITIONAL | FGI edition confirmation pending | Architect of Record (AOR) — AOR Project Architect | May 23, 2025 | Resolved
GR-0022 | HHC-SMR-006 | — | Schedule & Milestone Requirements | DD Phase | Generator Procurement | Schedule | Procurement — Long Lead | Generator procurement shall be initiated no later than October 31, 2025 (30% DD milestone). Procurement shall not begin before BCR-003 scope allocation is resolved. | Emergency Generator EQ-064 | Schedule sequencing — procurement lead time | Generator procurement deadline | Procurement initiated by October 31, 2025 | 30% DD milestone | Conditional on BCR-003 resolution | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-064 Equipment Schedule | Inspection | Gallant / Heritage PM — purchase order in project record by October 31, 2025 | 30% DD gate | Electrical / Program Management | Heritage Development Partners | TBD — see BCR-003 | Generator procurement scope unresolved per BCR-003 | DECISION-PENDING | Critical | Electrical / Cost / Schedule | NNN Lease — Exhibit D (TBD) | Medium | 20–28 week procurement lead. If not ordered by October 2025, generator cannot arrive for June 2026 construction start energize requirements. | 90 | Critical | LONG_LEAD ¦ DECISION_REQUIRED ¦ HIGH_COST_INFRASTRUCTURE | procurement initiated by Oct 31, 2025 | Y | CONDITIONAL | Procurement shall not begin before BCR-003 | Owner's PM (Heritage) + Tenant Facilities Lead (Northstar) | October 31, 2025 | Open
GR-0023 | HHC-SMR-007 | GR-0018 | Schedule & Milestone Requirements | DD Phase | RF Shielding Engagement | Schedule | Procurement — Long Lead | RF shielding specialty contractor shall be engaged no later than October 31, 2025 (30% DD). RF shielding engagement shall not precede MRI model confirmation (SMR-002). | RF Shielding System EQ-072 | Schedule sequencing — specialty contractor lead time | RF shielding contractor engagement deadline | Engaged by October 31, 2025 | 30% DD; conditional on GR-0018 (MRI model) resolved | MRI model must be confirmed first | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-072 Equipment Schedule | Inspection | Gallant — RF shielding contract in project record by October 31, 2025 | 30% DD gate | Architecture / Electrical | Northstar / GC Preconstruction | TI scope — specialty contractor | RF shielding spec is MRI-vendor-specific; all rough-in penetrations must be coordinated | DECISION-PENDING | High | Architecture / Electrical / Structural | TI scope — specialty sub | Medium | 12-week minimum lead. Shielding vendor and spec depend on confirmed MRI vendor per GR-0018. Conditional on OAI-001 resolution. | 85 | High | LONG_LEAD ¦ DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | engagement by Oct 31, 2025 | Y | CONDITIONAL | shall not precede MRI model confirmation | Northstar / GC Preconstruction | October 31, 2025 (after GR-0018) | Open
GR-0024 | HHC-SMR-008 | — | Schedule & Milestone Requirements | Construction | MRI Pre-Enclosure | Schedule | Construction Sequencing | MRI magnet shall be set in final installed position before final wall enclosure of the MRI magnet room. Wall enclosure shall not proceed until documented by dated field report and photographs. | MRI Magnet Room — Wall Enclosure Sequence | Construction sequencing — critical path | MRI pre-enclosure delivery sequence | Magnet set before wall enclosure | During clinical TI construction phase | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-020 Equipment Schedule | Inspection | CMAR Superintendent — field report and photographs dated prior to wall enclosure | MRI Magnet Room — construction phase | Architecture / Structural / CMAR | CMAR Superintendent — Cornerstone Construction | TI scope — Northstar (OFE) / GC coordination | CMAR construction schedule must reflect MRI delivery window before wall enclosure | GOVERNING | Critical | Structural / Architecture / CMAR Schedule | CMAR contract — construction milestone | High | If wall enclosure precedes MRI delivery, demolition required to install magnet. Cost and schedule impact would be severe. | 96 | Critical | LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION ¦ HIGH_COST_INFRASTRUCTURE | before wall enclosure | shall be set | prior to wall enclosure | — | — | — | N/A
GR-0025 | HHC-SMR-009 | — | Schedule & Milestone Requirements | Construction | Electrical Energize | Schedule | Construction Sequencing | Primary electrical service to the clinical tenant shall be energized no later than March 2027, providing minimum 90 days before targeted commissioning start. | Primary Electrical Service | Construction sequencing — commissioning dependency | Electrical energize deadline | Energized by March 2027 | Minimum 90 days before commissioning start (December 2027) | None | ProgramDoc | Heritage Health Campus Milestone Schedule v1.0 | MS-046 Milestone Schedule | Inspection | Utility / Electrical Sub — energize confirmation in project record; date verified against commissioning schedule | Construction phase | Electrical | Heritage Development Partners / Utility | Base building scope — Heritage | Electrical energize enables TAB and system testing before clinical commissioning | GOVERNING | High | Electrical / MEP / Commissioning | CMAR contract — construction milestone | High | 90-day minimum between energize and commissioning is consistent with industry practice for healthcare system startup. | 72 | High | MULTI_DISCIPLINE_COORDINATION | 90 days minimum | shall be energized | before commissioning start | — | — | — | N/A
GR-0026 | HHC-SMR-010 | — | Schedule & Milestone Requirements | SD Phase | 50% SD Deliverable | Schedule | Design Phase Gate | 50% SD deliverables including initial BOD narrative shall be submitted by A/E to Owner and Gallant no later than July 11, 2025. | 50% SD Submittal Package | Design phase gate — first formal output | 50% SD submission deadline | Submitted by July 11, 2025 | 10 weeks from A/E NTP (May 5, 2025) | None | ProgramDoc | Heritage Health Campus Milestone Schedule v1.0 | MS-024 Milestone Schedule | Inspection | Gallant / Owner — Procore transmittal record dated on or before July 11, 2025 | SD Phase | Architecture / A/E Team | Architect of Record (AOR) | A/E Contract scope | BOD is first design output; Gallant processes as source document for RIR Cycle 1 | GOVERNING | High | Architecture / All Disciplines | A/E Contract — phase gate | High | BOD becomes Document 8 in the register. RIR Cycle 1 follows within 14 days. | 68 | High | DECISION_REQUIRED ¦ SCOPE_GAP | submitted by July 11, 2025 | shall be submitted | by July 11, 2025 | — | — | — | N/A
GR-0027 | HHC-BCR-001 | — | Budget & Cost Requirements | Project Budget | TPC Authorization | Budget | Cost Control — Total Project | Total Project Cost shall not exceed $68,000,000 Board-authorized TPC. Variances exceeding 5% require written Board re-authorization before proceeding. | Total Project Cost | Cost control — TPC ceiling | Total project cost ceiling | $68,000,000 maximum | At all design and construction phases | None | OwnerBudgetAuth | Heritage Health Campus Programming Document v1.0 | §C Cost Estimates / Board Resolution 2024-11 | Analysis | Heritage Cost Consultant — third-party estimate at 60% DD and 90% CD | All project phases | Cost Management | Heritage Board of Managers | Heritage scope | All design decisions evaluated against TPC | GOVERNING | Critical | Cost / All Disciplines | Board Resolution 2024-11 | High | Current estimate $72M exceeds $68M ceiling by $4M (5.9%). VE-01 and generator cost split resolution required. BCR-CONFLICT-001 active. | 92 | Critical | HIGH_COST_INFRASTRUCTURE ¦ DECISION_REQUIRED | $68,000,000 maximum | shall not exceed | at all phases | — | — | — | N/A
GR-0028 | HHC-BCR-002 | GR-0027 | Budget & Cost Requirements | TI Allowance | Clinical TI Budget | Budget | Cost Control — Clinical TI | Clinical TI construction cost shall not exceed $14,200,000 TI Allowance per executed NNN lease Exhibit D. | Clinical TI Construction | Cost control — TI allowance | Clinical TI cost ceiling | $14,200,000 maximum | At all TI design and construction phases | None | OwnerBudgetAuth | Heritage Health Campus Programming Document v1.0 | §C / NNN Lease Exhibit D | Analysis | Heritage Cost Consultant — TI estimate at 60% DD reconciled against TI Allowance | Clinical TI phases | Cost Management | Heritage + Northstar | Northstar TI scope | All TI design decisions evaluated against TI Allowance | GOVERNING | Critical | Cost / Architecture / MEP / Structural | NNN Lease Exhibit D | High | Binding per executed lease. Scope additions above TI Allowance require joint written authorization from Heritage and Northstar. | 88 | Critical | HIGH_COST_INFRASTRUCTURE | $14,200,000 maximum | shall not exceed | all TI phases | — | — | — | N/A
GR-0029 | HHC-BCR-003 | GR-0027 | Budget & Cost Requirements | Generator | Scope Allocation | Budget | Cost Control — Generator | Generator scope allocation (200kW base building vs. 350kW combined EES minimum) shall be assigned in writing between Heritage and Northstar Owner's Reps prior to 50% SD gate approval. | Generator — Scope Allocation | Cost control — scope boundary | Generator upsize cost allocation | Written allocation of 200kW→350kW upsize cost delta | Prior to 50% SD gate | Exhibit D silent on generator upsize | OwnerBudgetAuth | Heritage Health Campus Programming Document v1.0 | §C / NNN Lease Exhibit D | Inspection | Gallant / Owner — written memo in project file before 50% SD gate | Pre-50% SD | Cost Management / Electrical | Heritage PM + Northstar Facilities | TBD — scope allocation required | Generator procurement and EES design blocked pending resolution | GOVERNING | Critical | Electrical / Cost / Schedule | NNN Lease Exhibit D (silent) | Medium | CONFLICT-C003 active. OPC estimates 150kW clinical; Programming Doc base building generator 200kW life safety; combined = 350kW minimum per NFPA 99. Cost delta est. $180K–$260K. Neither document assigns it. ¦ CLOSED by D11 Directive 5: BCR-003 RESOLVED. 350kW generator confirmed. Northstar bears upsize cost ($180K–$260K) from TI Allowance. CF-001 RESOLVED. | 93 | Critical | DECISION_REQUIRED ¦ HIGH_COST_INFRASTRUCTURE ¦ SCOPE_GAP | cost responsibility not assigned | N | EMBEDDED-CHOICE | shall be assigned in writing — cost delta not assigned | Owner's PM (Heritage) + Tenant Facilities Lead (Northstar) | July 11, 2025 | Resolved
GR-0030 | HHC-BCR-004 | GR-0027 | Budget & Cost Requirements | VE | Value Engineering | Budget | Cost Control — Value Engineering | DD cost estimate shall be reconciled against BCR-001. If variance exceeds 5%, A/E shall prepare VE options log for Owner review before CD NTP. | DD Cost Estimate | Cost control — VE gate | DD estimate reconciliation threshold | 5% variance triggers VE review | At 60% DD gate | None | ProgramDoc | Heritage Health Campus Programming Document v1.0 | §C Budget Variance Notice | Analysis | Heritage Cost Consultant — DD estimate + variance report | 60% DD gate | Cost Management | Heritage Development Partners | A/E Contract scope | VE-01 (foundation system) is the primary VE opportunity — contingent on geotechnical report | GOVERNING | High | Cost / All Disciplines | A/E Contract — phase gate | High | VE-01 potential savings $180K–$340K pending geotech confirmation of Site Class C+. | 65 | High | HIGH_COST_INFRASTRUCTURE ¦ SCOPE_GAP | 5% threshold | shall prepare VE options | at 60% DD | — | — | — | N/A
GR-0031 | HHC-PIR-001 | — | Physical & Interface Requirements | Space Program | Clinical GSF | Physical | Space Program | Clinical tenant improvement shall achieve total 24,000 GSF across Floors 1 and 2. A/E shall report any deviation from GSF target to both Heritage and Northstar at 50% SD. | Clinical TI — Total Area | Space program compliance | Total clinical GSF | 24,000 GSF | Floors 1 and 2 | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §2 Space Program | Analysis | Architect of Record (AOR) — area takeoff at 50% SD verified against 24,000 GSF | SD Phase | Architecture | Architect of Record (AOR) | TI scope — Northstar | Floor plate configuration and gross-up factor (22%) govern NSF targets | GOVERNING | High | Architecture | NNN Lease — demised premises | High | 13,740 NSF target with 22% gross-up = 24,000 GSF. Deviation from GSF target must be reported before SD completion. | 68 | High | SCOPE_GAP | 24,000 GSF | shall achieve | Floors 1 and 2 | — | — | — | N/A
GR-0032 | HHC-PIR-002 | GR-0031 | Physical & Interface Requirements | Space Program | Exam Room NSF | Physical | Space Program — Exam Rooms | Exam rooms shall provide minimum 100 NSF clear floor area exclusive of toilet rooms and casework. Four accessible exam rooms shall provide minimum 140 NSF. | Exam Rooms (16 total) | Space program compliance | Exam room minimum clear floor area | 100 NSF standard / 140 NSF accessible (4 rooms) | All 16 exam rooms | Exclusive of toilet rooms and fixed casework | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-006 / FGI 2022 §2.1-3.2.2.2 | Inspection | Architect of Record (AOR) — dimension verification at SD floor plan and field measurement | All exam rooms | Architecture | Architect of Record (AOR) | TI scope — Northstar | Exam room dimensions drive primary care suite NSF allocation | GOVERNING | High | Architecture | NNN Lease — TI scope | High | FGI 2022 minimum. 4 accessible rooms require 140 NSF for height-adjustable table and 60-in. turning radius. | 72 | High | REGULATORY_APPROVAL | 100 NSF / 140 NSF | shall provide | all 16 exam rooms | — | — | — | N/A
GR-0033 | HHC-PIR-003 | GR-0002 | Physical & Interface Requirements | Imaging Suite | MRI Room Dimensions | Physical | Space Program — Imaging | MRI suite minimum net areas: Magnet Room 700 NSF; Equipment Room 200 NSF (NOTE: GE SIGNA option requires 240 NSF — see OAI-001); Control Room 150 NSF. | MRI Suite — Room Dimensions | Space program compliance | MRI suite room minimum areas | Magnet: 700 NSF / Equipment: 200 NSF (Siemens) or 240 NSF (GE) / Control: 150 NSF | MRI suite, Floor 2 | GE option creates 40 NSF conflict with OPC program | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-020 EQ-021 EQ-022 Equipment Schedule | Inspection | Architect of Record (AOR) — area takeoff at SD + field measurement | MRI Suite, Floor 2 | Architecture | Architect of Record (AOR) | TI scope — Northstar | MRI room dimensions affect imaging suite floor plan and adjacent space allocation | GOVERNING | High | Architecture / Structural | NNN Lease — TI scope | Medium | CONFLICT-C002 active: OPC programs 200 NSF equipment room; GE SIGNA option requires 240 NSF. Vendor selection per OAI-001 resolves conflict. ¦ CLOSED by D11: MRI equipment room 200 NSF confirmed for Siemens MAGNETOM Altea. CF-002 RESOLVED. | 90 | High | DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | 200 NSF (Siemens) vs. 240 NSF (GE) | N | TBD-UNRESOLVED | 200 NSF (Siemens) vs. 240 NSF (GE) — vendor TBD | Northstar Biomedical Engineering (via GR-0018) | June 13, 2025 (per SMR-002) | Resolved
GR-0034 | HHC-PIR-004 | GR-0003 | Physical & Interface Requirements | Physical Therapy | PT Gym Dimensions | Physical | Space Program — PT | PT open gym shall provide minimum 1,200 NSF with minimum 10-foot clear ceiling height. No structural columns shall intrude into the open gym area. | PT Open Gym | Space program compliance | PT gym minimum area and ceiling height | 1,200 NSF / 10 ft clear ceiling minimum / column-free | PT open gym area | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §C Physical Therapy Suite | Inspection | AOR + SER — area, ceiling height, and column-free verified at SD | PT Suite | Architecture / Structural | Architect of Record (AOR) | TI scope — Northstar | Column-free requirement affects structural framing layout above Level 2 | GOVERNING | High | Architecture / Structural | NNN Lease — TI scope | High | Column-free requirement may affect structural framing design on Level 2 and above. Coordinate with structural engineer. | 68 | High | MULTI_DISCIPLINE_COORDINATION | 1,200 NSF / 10 ft clear / column-free | shall provide | PT open gym | — | — | — | N/A
GR-0035 | HHC-PIR-005 | — | Physical & Interface Requirements | Circulation | Corridor Width | Physical | Architecture — Circulation | Clinical patient corridors on Floors 1 and 2 shall be minimum 8 feet (96 inches) clear width. Staff-only and back-of-house corridors shall be minimum 44 inches clear. | Clinical Corridors | Circulation — egress and code compliance | Corridor minimum clear width | 8 ft patient / 44 in staff minimum clear | All clinical floors | Conditional on AHC occupancy confirmation per GR-0042 | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-011 / NFPA 101 §20.2.3 | Inspection | Architect of Record (AOR) — dimension verification at SD floor plan and field measurement | Floors 1 and 2 | Architecture | Architect of Record (AOR) | TI scope — Northstar | 8-ft corridors are AHC occupancy requirement. If Group B is confirmed, 44 in. is sufficient. | GOVERNING | Critical | Architecture / Structural | NNN Lease — TI scope | High | DF-001: AHC occupancy assumed pending AHJ confirmation per GR-0042. 8-ft corridor widths designed on AHC basis. If Group B confirmed, SD corridor widths may be revised. ¦ CLOSED by D9: AHC occupancy confirmed → 96-inch (8-foot) corridor requirement locked. DF-001 RESOLVED. ¦ CLOSED by D9: AHC occupancy confirmed → 96-inch (8-foot) corridor requirement locked. DF-001 RESOLVED. | 88 | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | 8 ft / 96 in. minimum clear | N | CONDITIONAL | conditional on AHC occupancy confirmation | AOR + NM DOH (AHJ response) | Per SMR-005 — May 23, 2025 | Resolved
GR-0036 | HHC-PIR-006 | — | Physical & Interface Requirements | HVAC | Clinical AHU Separation | Physical | Mechanical — System Separation | Dedicated AHUs serving the clinical component shall be physically and ductwork-separated from residential and retail HVAC systems. Clinical AHUs located in dedicated mechanical room. | Clinical AHU Systems | Physical system separation | Clinical HVAC physical isolation from other occupancies | Dedicated AHUs, separate ductwork, dedicated mechanical room | All operating conditions | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.1 HVAC | Inspection | MEP Engineer of Record (MEP-EOR) — verified at DD mechanical drawings and field inspection | Clinical AHU mechanical room, Floors 1–2 | Mechanical | MEP Engineer of Record (MEP-EOR) | TI scope / Base Building interface — see CONFLICT-C003 | AHU procurement boundary between base building and TI scope is unresolved — CONFLICT-C003 active | GOVERNING | High | Mechanical / Architecture / Cost | NNN Lease Exhibit D (silent on AHU procurement) | Medium | CONFLICT-C003 active: OPC requires dedicated clinical AHUs; Exhibit D silent on whether AHUs are Landlord Work or Tenant Work. Procurement authority and cost assignment unresolved. | 82 | High | SCOPE_GAP ¦ DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | dedicated AHUs / separated ductwork | Y | EMBEDDED-CHOICE | Exhibit D is silent — procurement boundary not assigned | Owner's PM (Heritage) + Tenant Facilities Lead (Northstar) | July 11, 2025 | Open
GR-0037 | HHC-PIR-007 | — | Physical & Interface Requirements | Plumbing | Water Riser | Physical | Plumbing — Infrastructure | A separate domestic water riser shall serve clinical Floors 1 and 2. An isolation valve accessible without entering clinical patient areas shall be provided at the base of the clinical riser. | Domestic Water Riser — Clinical | Physical infrastructure separation | Separate clinical water riser with isolation valve | Separate riser + isolation valve accessible from non-clinical area | All operating conditions | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.3 Plumbing | Inspection | MEP Engineer of Record (MEP-EOR) — verified at field inspection at substantial completion | Clinical floors water riser location | Plumbing | MEP Engineer of Record (MEP-EOR) | Base building scope — Heritage (riser) / TI scope — Northstar (distribution) | Riser is base building scope; distribution within clinical TI scope | GOVERNING | Moderate | Plumbing | NNN Lease — base building / TI boundary | High | Isolation valve accessibility is critical for maintenance and emergency shutoff without entering clinical areas. | 48 | Moderate | MULTI_DISCIPLINE_COORDINATION | separate riser + accessible isolation valve | shall serve | clinical Floors 1 and 2 | — | — | — | N/A
GR-0038 | HHC-PIR-008 | — | Physical & Interface Requirements | Medical Gas | Rough-In Locations | Physical | Plumbing — Medical Gas | Medical gas rough-in (O₂ outlet + vacuum outlet) shall be provided at minimum: isolation room (1 each), MRI patient prep/recovery bays (2 bays, 1 each). Additional locations per OAI-004. | Medical Gas Outlets — Minimum Locations | Physical infrastructure — medical gas | Medical gas outlet minimum location requirement | O₂ + vacuum at isolation room and 2 MRI prep/recovery bays | Per OAI-004 scope confirmation | OAI-004: additional locations under review | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.3 Plumbing OAI-004 | Inspection | MEP Engineer of Record (MEP-EOR) — field verification at rough-in and substantial completion | Isolation room + MRI prep/recovery bays | Plumbing | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | NFPA 99 Category 1 compliance; medical gas contractor engagement required | DECISION-PENDING | High | Plumbing / MEP | NNN Lease — TI scope | Medium | OAI-004: Northstar clinical director to confirm whether additional medical gas locations are required beyond isolation room and MRI prep. Open action item. | 72 | High | REGULATORY_APPROVAL ¦ DECISION_REQUIRED | O₂ + vacuum minimum locations | Y | TBD-UNRESOLVED | additional locations per OAI-004 | Northstar Clinical Director | Prior to 50% SD | Open
GR-0039 | HHC-PIR-009 | GR-0002 | Physical & Interface Requirements | Structural | MRI Point Load | Physical | Structural — MRI | MRI magnet room structural design shall accommodate the magnet point load with a dedicated vibration isolation system. Structural design shall not be finalized without confirmed vendor data sheet. | MRI Magnet Room — Structure | Physical structural design | MRI point load structural accommodation | 25,000 lb total est. (vendor-specific: Siemens 7,700 lb magnet / GE 8,100 lb magnet) | MRI magnet room floor and foundation | Conditional on MRI vendor confirmation GR-0018 | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-020 Equipment Schedule | Analysis | Structural Engineer of Record (SER) — structural calculations submitted at 30% DD confirming point load design | MRI Magnet Room structural elements | Structural | Structural Engineer of Record (SER) | TI scope — structural reinforcement / Base building — podium slab | Vibration isolation system is MRI-vendor-specific; inertia slab or isolated pad | GOVERNING | Critical | Structural / MEP / Architecture | A/E Contract — structural engineering scope | Medium | CONFLICT-C004 active: Equipment Schedule lists both Siemens (7,700 lb) and GE (8,100 lb) as under evaluation — two conflicting structural design basis values. Structural engineer proceeding on Siemens basis pending vendor confirmation. ¦ CLOSED by D11: Siemens MAGNETOM Altea confirmed — PIR-009 equipment room area locked at 200 NSF. | 95 | Critical | DECISION_REQUIRED ¦ LONG_LEAD ¦ HIGH_COST_INFRASTRUCTURE ¦ MULTI_DISCIPLINE_COORDINATION | 25,000 lb point load (vendor TBD) | N | TBD-UNRESOLVED | 25,000 lb point load — vendor-specific per OAI-001 | Northstar Biomedical Engineering (via GR-0018) | June 13, 2025 | Resolved
GR-0040 | HHC-PIR-010 | — | Physical & Interface Requirements | Structural | PT Hydrotherapy Slab | Physical | Structural — PT | PT hydrotherapy whirlpool area structural slab shall be rated for minimum 150 psf plus water load of installed unit (EQ-046, est. 900 lbs full). Waterproof membrane under all tile finishes. | PT Hydrotherapy Slab | Physical structural design | Hydrotherapy area structural floor rating | 150 psf + 900 lb water load / waterproof membrane required | PT hydrotherapy area | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-046 Equipment Schedule | Inspection | SER — calculation at 30% DD; waterproof membrane inspection at substantial completion | PT Hydrotherapy Area | Structural / Architecture | Structural Engineer of Record (SER) | TI scope — Northstar | Structural slab design + waterproof membrane + floor drain coordination | GOVERNING | High | Structural / Architecture / Plumbing | NNN Lease — TI scope | High | 900 lb at full load. Structural engineer must confirm slab capacity at 30% DD narratives. | 65 | High | HIGH_COST_INFRASTRUCTURE | 150 psf + 900 lb water load | shall be rated | PT hydrotherapy area | — | — | — | N/A
GR-0041 | HHC-PIR-011 | — | Physical & Interface Requirements | OFE Integration | Equipment Input Drawings | Physical | OFE Coordination | All OFE items in Equipment Schedule v1.0 shall be reflected in A/E Construction Documents with confirmed facility input requirements (electrical, plumbing, structural, data) by 50% CD. | All OFE Equipment Items | OFE coordination — facility inputs | OFE facility input integration deadline | All 56 Equipment Schedule items reflected in CDs with confirmed inputs | 50% CD submittal | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | Equipment Schedule v1.0 — all EQ items | Inspection | Architect of Record (AOR) — OFE facility input drawings in 50% CD submittal | All clinical spaces, Floors 1–2 | Architecture / All Engineering | Architect of Record (AOR) (coordination lead) | TI scope — A/E coordination | OFE input drawings must be received from vendors before 50% CD | GOVERNING | High | Architecture / Structural / MEP / Electrical / IT | A/E Contract — OFE coordination scope | High | Equipment Schedule v1.0 lists 56 items. Each requires facility inputs in applicable discipline CDs. DECISION-PENDING items (MRI, PT additions) cannot be final until vendor/owner confirmed. | 68 | High | MULTI_DISCIPLINE_COORDINATION ¦ LONG_LEAD | reflected in CDs by 50% CD | shall be reflected | 50% CD submittal | — | — | — | N/A
GR-0042 | HHC-RCR-001 | — | Regulatory & Compliance Requirements | TJC AHC | Accreditation Framework | Regulatory | TJC — Accreditation | The clinic shall comply with all Joint Commission Ambulatory Health Care accreditation standards applicable to a new facility providing primary care, imaging, and physical therapy. | Clinic — TJC AHC Compliance | Regulatory compliance — accreditation | TJC AHC compliance framework | Full TJC AHC accreditation standards | Day 1 of operations and ongoing | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-001 / TJC AHC Program | Demonstration | TJC AHC accreditation survey result — Day 1 | Floors 1–2, all clinical spaces | All disciplines | Northstar Health System — Compliance | TI scope | 52 sub-requirements trace to this governing requirement | GOVERNING | Critical | All disciplines | NNN Lease — Day 1 accreditation target | High | Top-level accreditation requirement. All RCR requirements in sections §1–§6 of TJC document trace here. | 98 | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY | shall comply | shall achieve | Day 1 operations | — | — | — | N/A
GR-0043 | HHC-RCR-002 | GR-0042 | Regulatory & Compliance Requirements | FGI | Governing Standard | Regulatory | Code — FGI Edition | The clinical facility design shall comply with the applicable edition of FGI Guidelines for Design and Construction of Outpatient Facilities as confirmed by NM DOH AHJ. Planning basis: FGI 2022. | Clinical Design — FGI Edition | Regulatory compliance — governing design standard | FGI edition compliance | FGI 2022 (planning basis) or FGI 2018 (if AHJ confirms 2018 adoption) | SD through CD phases | AHJ confirmation of adopted edition required | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-002 / FGI 2022 Outpatient | Inspection | AOR — AHJ written confirmation of applicable edition in project record before 50% SD | Pre-50% SD | Architecture | Architect of Record (AOR) | A/E Contract scope | Edition affects corridor widths, imaging room classifications, and ICRA requirements | GOVERNING | High | Architecture / Regulatory | A/E Contract — code compliance | Medium | DF-NEW-001: NM DOH not confirmed to have adopted FGI 2022. Kickoff meeting identified FGI 2018 may govern. AHJ pre-application required per SMR-005. ¦ CLOSED by D9: FGI 2022 confirmed governing by NM DOH. NM-CID-HFS-2025-0603-HHC §2. ¦ CLOSED by D9: FGI 2022 confirmed governing by NM DOH. NM-CID-HFS-2025-0603-HHC §2. | 92 | High | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | FGI 2022 planning basis — AHJ confirmation pending | N | CONDITIONAL | FGI 2022 planning basis — AHJ confirmation pending | Architect of Record (AOR) (AHJ submission) | May 23, 2025 | Resolved
GR-0044 | HHC-RCR-003 | GR-0043 | Regulatory & Compliance Requirements | Occupancy | AHC Classification | Regulatory | Code — Occupancy Classification | Floors 1–2 clinical occupancy shall be classified as AHC per NFPA 101 Chapter 20. Classification shall be confirmed with NM DOH before SD corridor widths and egress design are finalized. | Clinical Occupancy Classification | Regulatory compliance — NFPA 101 occupancy | AHC occupancy classification | NFPA 101 Chapter 20 AHC — subject to AHJ confirmation | All construction and operation phases | Conditional on AHJ pre-application response | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-004 / NFPA 101 Ch. 20 | Inspection | AHJ — written occupancy confirmation in project record | Floors 1–2 | Architecture / Fire Protection | Architect of Record (AOR) | A/E Contract scope | Drives 8-ft corridor width, egress design, and sprinkler system design | GOVERNING | Critical | Architecture / Fire Protection / MEP | A/E Contract — code basis | Medium | DF-001: AHC assumed. If AHJ confirms Group B, corridor widths change from 8 ft to 44 in. Design on AHC basis per GR-0035 until confirmed. ¦ CLOSED by D9: AHC occupancy under NFPA 101 Chapter 20 confirmed for Floors 1-2. DF-001 RESOLVED. ¦ CLOSED by D9: AHC occupancy under NFPA 101 Chapter 20 confirmed for Floors 1-2. DF-001 RESOLVED. | 90 | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | AHC classification assumed | N | CONDITIONAL | AHC classification assumed — pending AHJ confirmation | Architect of Record (AOR) (AHJ response) | Per SMR-005 | Resolved
GR-0045 | HHC-RCR-004 | GR-0042 | Regulatory & Compliance Requirements | NFPA 99 | Healthcare Facilities Code | Regulatory | Code — NFPA 99 | Clinical areas shall comply with NFPA 99 (2021) for medical gas systems, Category 1 EES, equipment grounding in all patient care spaces, and IPS in imaging areas. | Clinical Areas — NFPA 99 Compliance | Regulatory compliance — healthcare facilities code | NFPA 99 Category 1 compliance | Full NFPA 99 (2021) compliance — medical gas, EES, grounding, IPS | All clinical areas, Floors 1–2 | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-005 / NFPA 99 (2021) | Test + Inspection | MEP Engineer of Record (MEP-EOR) — NFPA 99 compliance matrix at 90% CD + commissioning functional tests | All clinical areas | Electrical / Plumbing | MEP Engineer of Record (MEP-EOR) | TI scope — clinical EES / Base building — generator | Generator capacity is the critical NFPA 99 Category 1 constraint — see BCR-003 | GOVERNING | Critical | Electrical / Plumbing / Architecture | NNN Lease — TI scope (EES) / Base building (generator) | High | Category 1 EES requires generator backup for clinical loads. See GR-0029 (BCR-003) for generator scope conflict. | 92 | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY ¦ HIGH_COST_INFRASTRUCTURE | Category 1 EES / NFPA 99 | shall comply | all clinical areas | — | — | — | N/A
GR-0046 | HHC-RCR-005 | GR-0044 | Regulatory & Compliance Requirements | Egress | Life Safety | Regulatory | Life Safety — Egress | Clinical occupancy egress shall comply with NFPA 101 Chapter 20. Exit travel distance shall not exceed 150 ft. Minimum 2 enclosed exit stairs with pressurization per IBC §909. | Egress — Clinical Floors | Life safety — egress design | Egress travel distance and stair requirements | 150 ft max travel distance / 2 enclosed stairs / pressurized per IBC §909 | All clinical floors | Conditional on AHC occupancy per GR-0044 | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-004 / NFPA 101 §20.2.5 / IBC 2021 §909 | Analysis + Inspection | Architect of Record (AOR) — egress travel distance at SD + AHJ final acceptance | Floors 1–2 | Architecture / Fire Protection | Architect of Record (AOR) | Base building scope — egress stairs / TI scope — clinical exit access | Shared egress stairs between clinical and residential — DF-003 watch item | GOVERNING | Critical | Architecture / Fire Protection | A/E Contract — code compliance | High | DF-003: shared egress stairs between clinical and residential occupancies — stair pressurization design not confirmed at SD. | 90 | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | 150 ft max / 2 stairs / pressurized | shall comply | conditional on AHC confirmation | — | — | — | N/A
GR-0047 | HHC-RCR-006 | GR-0042 | Regulatory & Compliance Requirements | Sprinkler | Fire Protection | Regulatory | Fire Protection — Sprinkler | Clinical component shall have full automatic sprinkler protection per NFPA 13. Separate sprinkler risers shall serve clinical (Floors 1–2) and residential (Floors 3–7) occupancies. | Fire Sprinkler System | Fire protection — sprinkler compliance | NFPA 13 full coverage with separate risers | NFPA 13 full coverage / separate clinical and residential risers | All clinical areas | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-012 / NFPA 13 | Inspection | Fire Protection Engineer — sprinkler permit drawings + AHJ final acceptance | Floors 1–2 (clinical riser) + Floors 3–7 (residential riser) | Fire Protection / Architecture | Fire Protection Engineer | Base building scope — risers / TI scope — clinical sprinkler heads and branch piping | Separate risers required; base building scope | GOVERNING | Critical | Fire Protection / Architecture | NNN Lease — base building scope | High | Separate risers ensure clinical sprinkler system can be isolated and maintained independently of residential. | 88 | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | NFPA 13 / separate risers | shall have full protection | Floors 1–7 | — | — | — | N/A
GR-0048 | HHC-RCR-007 | GR-0043 | Regulatory & Compliance Requirements | Imaging | FGI Class 1/2 | Regulatory | Code — Imaging Classification | Imaging suite shall include one Class 1 diagnostic radiography room and one Class 2 imaging room per FGI 2022 §2.3. Lead shielding by qualified radiation physicist. | Imaging Suite — Room Classification | Regulatory compliance — imaging room standards | Imaging room FGI classification | Class 1 (X-ray) + Class 2 (MRI) per FGI 2022 §2.3 | Imaging suite, Floor 2 | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-013 / FGI 2022 §2.3 | Analysis + Inspection | Northstar (radiation physicist report) + AOR (shielding in CDs) | Imaging Suite, Floor 2 | Architecture / Structural | Architect of Record (AOR) | TI scope — Northstar | Lead shielding in X-ray room; RF shielding in MRI room — both specialty contractor scope | GOVERNING | High | Architecture / Structural / Electrical | NNN Lease — TI scope | High | Radiation physicist engagement required for X-ray shielding. RF shielding by specialty contractor per GR-0023. | 88 | High | REGULATORY_APPROVAL ¦ LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION | Class 1 + Class 2 / lead and RF shielding | shall include | Imaging Suite | — | — | — | N/A
GR-0049 | HHC-RCR-008 | GR-0048 | Regulatory & Compliance Requirements | MRI | ACR Siting | Regulatory | Code — MRI Standards | MRI siting shall comply with ACR Technical Standard for Diagnostic MRI. Zone IV access shall be controlled. Ferromagnetic screening at Zone II/III boundary. | MRI Zone Access Control | Regulatory compliance — MRI safety | MRI zone safety and access control | ACR Zone I–IV compliance / controlled access Zone III and IV | All MRI operations | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-014 / ACR MRI Siting Standard | Inspection | AOR — zone diagram in CDs; access control verified at commissioning | MRI Suite, Floor 2 | Architecture / Electrical | Architect of Record (AOR) | TI scope — Northstar | MRI zone boundaries and access control drive floor plan and security infrastructure | GOVERNING | Critical | Architecture / Electrical / Safety | NNN Lease — TI scope | High | ACR zone diagram must appear in CDs. Zone III card reader or keypad required per SLR-004. | 92 | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | Zone I–IV compliance / ACR Standard | shall comply | MRI suite | — | — | — | N/A
GR-0050 | HHC-RCR-009 | — | Regulatory & Compliance Requirements | Acoustic | Clinical/Residential STC | Regulatory | Acoustic — Separation Assembly | Floor/ceiling assembly between Level 2 clinical and Level 3 residential shall achieve minimum STC 60 / IIC 55. Post-tensioned flat plate alone does not achieve this — acoustic overlay required. | Level 2/3 Floor/Ceiling Assembly | Regulatory compliance — acoustic separation | Clinical-to-residential acoustic assembly performance | STC 60 / IIC 55 minimum | Between Level 2 (clinical) and Level 3 (residential) at all times | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-019 / FGI 2022 Table 1-7A | Analysis + Test | Acoustic subconsultant — calculation at DD + field measurement at commissioning | Level 2 slab / Level 3 floor assembly | Structural / Architecture / Acoustic | Acoustic Subconsultant + Structural Engineer of Record (SER) | Base building scope — structural slab / TI scope — acoustic overlay | Acoustic overlay or floating floor system required on residential side. Cost in base building or residential TI scope. | GOVERNING | High | Structural / Architecture / Acoustic / Cost | NNN Lease — scope TBD | Medium | PT flat plate alone insufficient per BOD narrative. Acoustic overlay adds cost ($80K–$150K est.). Scope responsibility unclear between base building and residential TI. | 90 | High | HIGH_COST_INFRASTRUCTURE ¦ REGULATORY_APPROVAL ¦ SCOPE_GAP | STC 60 / IIC 55 | shall achieve | Level 2/3 assembly | — | — | — | N/A
GR-0051 | HHC-RCR-010 | GR-0042 | Regulatory & Compliance Requirements | Hand Hygiene | Sinks | Regulatory | Code — Infection Control | Hand-washing sinks shall be provided in every exam room, treatment room, triage room, and isolation room. Placement governed by ICRA per FGI 2022 §2.1-7.2.2.8. | Hand-Washing Sinks — Clinical Rooms | Regulatory compliance — HAI prevention | Hand-washing sink location requirements | One hand-washing sink per clinical room per ICRA | All clinical spaces | ICRA governs exact placement | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-007 / FGI 2022 §2.1-7.2.2.8 | Inspection | AOR — ICRA governs placement; field verification at substantial completion | All clinical rooms | Architecture / Plumbing | Northstar Infection Preventionist (ICRA) + AOR | TI scope — Northstar | Sink count drives plumbing rough-in and clinical water demand | DECISION-PENDING | High | Architecture / Plumbing | NNN Lease — TI scope | Medium | Conditional on ICRA completion per GR-0019. ICRA not yet received — final sink placement DECISION-PENDING. | 75 | High | REGULATORY_APPROVAL ¦ DECISION_REQUIRED | one sink per clinical room | Y | CONDITIONAL | placement governed by ICRA — not yet received | Northstar Infection Preventionist | June 27, 2025 (per SMR-003) | Open
GR-0052 | HHC-RCR-011 | GR-0010 | Regulatory & Compliance Requirements | HVAC | ASHRAE 170 | Regulatory | Code — HVAC Standard | Clinical areas shall comply with ANSI/ASHRAE/ASHE Standard 170 (2021) ventilation requirements. HVAC design shall meet minimum ACH, OA fraction, pressure relationship, and filtration per ASHRAE 170 Table 7.1. | Clinical HVAC System | Regulatory compliance — HVAC standard | ASHRAE 170 Table 7.1 compliance | Full ASHRAE 170 Table 7.1 compliance for all clinical space types | All clinical areas, all operating conditions | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-009 / ASHRAE 170-2021 | Test | MEP Engineer of Record (MEP-EOR) — TAB report demonstrating ASHRAE 170 compliance at commissioning | All clinical areas | Mechanical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | ASHRAE 170 compliance matrix required in 90% CD submittal | GOVERNING | High | Mechanical | NNN Lease — TI scope | High | TJC AHC accreditation requires ASHRAE 170 compliance. Non-compliance at commissioning is a TJC survey finding. | 88 | High | REGULATORY_APPROVAL ¦ LIFE_SAFETY | ASHRAE 170 Table 7.1 | shall comply | all clinical areas | — | — | — | N/A
GR-0053 | HHC-RCR-012 | — | Regulatory & Compliance Requirements | Plumbing | Fluid Disposal Sinks | Regulatory | Code — Plumbing | A fluid disposal sink (hopper/clinical sink) shall be provided in primary care soiled utility room and imaging soiled utility room per FGI 2022 §2.1-7.3. | Fluid Disposal Sinks | Regulatory compliance — clinical plumbing | Fluid disposal sink location | One hopper in primary care soiled utility + one in imaging soiled utility | Both soiled utility rooms, Floors 1 and 2 | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-010 / FGI 2022 §2.1-7.3 | Inspection | AOR — field verification at SD floor plan and substantial completion | Primary Care Soiled Utility + Imaging Soiled Utility | Architecture / Plumbing | Architect of Record (AOR) | TI scope — Northstar | Floor-mounted hoppers with flushing rim; floor drain within 18 in. required | GOVERNING | Moderate | Architecture / Plumbing | NNN Lease — TI scope | High | FGI 2022 mandatory requirement. Two locations confirmed per OPC §4.3. | 58 | Moderate | REGULATORY_APPROVAL | one per soiled utility room | shall be provided | primary care and imaging soiled utilities | — | — | — | N/A
GR-0054 | HHC-RCR-013 | GR-0042 | Regulatory & Compliance Requirements | ADA | Accessibility | Regulatory | Code — ADA | All clinical spaces shall comply with 2010 ADA Standards for Accessible Design. Minimum 60-in. turning radius in all exam rooms, treatment rooms, and patient toilet rooms. | Clinical Spaces — ADA Compliance | Regulatory compliance — accessibility | ADA accessible design | 2010 ADA Standards / 60-in. turning radius minimum | All clinical spaces | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-025 / ADA 2010 Standards | Inspection | AOR — ADA compliance review at SD + field measurement at substantial completion | All clinical spaces | Architecture | Architect of Record (AOR) | TI scope — Northstar | ADA turning radius drives minimum room NSF; 140 NSF for accessible exam rooms | GOVERNING | High | Architecture | NNN Lease — TI scope | High | Federal law requirement. 4 accessible exam rooms require 140 NSF per GR-0032. | 80 | High | REGULATORY_APPROVAL | 2010 ADA / 60-in. turning radius | shall comply | all clinical spaces | — | — | — | N/A
GR-0055 | HHC-RCR-014 | GR-0053 | Regulatory & Compliance Requirements | Plumbing | Toilet Room Ratio | Regulatory | Code — Patient Toilet Rooms | Patient toilet rooms shall be provided at minimum 1 per 6 exam rooms per FGI 2022 §2.1-3.2. All accessible. One with bariatric clearances (60-in. turning radius minimum). | Patient Toilet Rooms | Regulatory compliance — toilet room ratio | Patient toilet room quantity and accessibility standard | 1 per 6 exam rooms minimum / all accessible / 1 bariatric | Clinical floors | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-026 / FGI 2022 §2.1-3.2 | Inspection | AOR — toilet room count and clearances at SD floor plan | Floors 1–2 | Architecture | Architect of Record (AOR) | TI scope — Northstar | 16 exam rooms = minimum 3 patient toilet rooms required; OPC programs 3 on Floor 1 | GOVERNING | High | Architecture | NNN Lease — TI scope | High | 1:6 ratio means 3 toilet rooms minimum for 16 exam rooms. OPC programs 3 accessible rooms on Floor 1. | 72 | High | REGULATORY_APPROVAL | 1 per 6 exam rooms / bariatric clearances | shall be provided | Floors 1–2 | — | — | — | N/A
GR-0056 | HHC-RCR-015 | GR-0052 | Regulatory & Compliance Requirements | EES | Category 1 | Regulatory | Code — Essential Electrical | Clinical floors shall be served by Category 1 Essential Electrical System per NFPA 99. Dedicated ATS for clinical EES, separate from residential. Generator per BCR-003 decision. | Essential Electrical System | Regulatory compliance — EES | Category 1 EES compliance | NFPA 99 Category 1 / dedicated clinical ATS / generator per BCR-003 | All clinical areas during and after normal power interruption | Conditional on BCR-003 generator resolution | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-016 / NFPA 99 Category 1 | Test | MEP Engineer of Record (MEP-EOR) (Electrical) — EES functional test at commissioning | Clinical Floors 1–2 | Electrical | MEP Engineer of Record (MEP-EOR) | TI scope — ATS and distribution / Base building — generator per BCR-003 | Generator scope per BCR-003 allocation unresolved | DECISION-PENDING | Critical | Electrical / Cost | NNN Lease Exhibit D (partially silent) | Medium | Conditional on BCR-003 resolution. 350kW generator required for NFPA 99 Category 1 compliance but cost not assigned. See GR-0029. | 92 | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY ¦ HIGH_COST_INFRASTRUCTURE | Category 1 EES / 350kW generator | Y | CONDITIONAL | conditional on BCR-003 generator resolution | Owner's PM + Tenant Facilities Lead (per BCR-003) | July 11, 2025 | Open
GR-0057 | HHC-SER-001 | — | Sustainability & Environmental Requirements | Energy | ASHRAE 90.1 | Sustainability | Code — Energy | The building shall comply with ASHRAE 90.1-2019 as adopted by the City of Albuquerque. Energy compliance report shall be included in the 90% CD submittal. | Building Energy Performance | Sustainability — energy code compliance | ASHRAE 90.1-2019 compliance | Full ASHRAE 90.1-2019 compliance per City of Albuquerque adoption | Design through construction | None | ProgramDoc | Heritage Health Campus Programming Document v1.0 | §C / City of Albuquerque energy code | Analysis | MEP Engineer of Record (MEP-EOR) — energy compliance report at 90% CD | All building occupancies | Mechanical / Electrical | MEP Engineer of Record (MEP-EOR) | Base building and TI scope | Energy compliance applies to base building and clinical TI HVAC and lighting | GOVERNING | Moderate | Mechanical / Electrical | A/E Contract — code compliance | High | City of Albuquerque has adopted ASHRAE 90.1-2019. Compliance demonstration required in 90% CD. | 48 | Moderate | REGULATORY_APPROVAL | ASHRAE 90.1-2019 | shall comply | design through construction | — | — | — | N/A
GR-0058 | HHC-SER-002 | — | Sustainability & Environmental Requirements | Waterproofing | PT Hydrotherapy | Sustainability | Architecture — Waterproofing | PT hydrotherapy area shall have waterproof membrane beneath all floor and wall tile finishes, extending minimum 18 in. above finished floor on all walls. Floor sloped to drain at minimum 1/8 in./ft. | PT Hydrotherapy Waterproofing | Environmental protection — water damage prevention | Waterproof membrane and floor slope | Waterproof membrane + 18-in. wall coverage + 1/8-in./ft minimum slope | PT hydrotherapy area | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §C Physical Therapy Suite | Inspection | AOR / Owner's Rep — membrane inspection before tile installation | PT Hydrotherapy Area | Architecture | Architect of Record (AOR) | TI scope — Northstar | Waterproof membrane is a prerequisite for tile installation; inspection required before covering | GOVERNING | Moderate | Architecture / Plumbing | NNN Lease — TI scope | High | Critical construction quality requirement. Membrane must be inspected and approved before tile goes on. | 45 | Moderate | — | waterproof membrane + 18 in. wall coverage | shall have | PT hydrotherapy area | — | — | — | N/A
GR-0059 | HHC-SER-003 | — | Sustainability & Environmental Requirements | Drainage | Floor Drains | Sustainability | Plumbing — Floor Drains | Floor drains shall be provided in: PT hydrotherapy area, primary care soiled utility room, imaging soiled utility room, and all janitor's closets (one per floor). | Floor Drains — Required Locations | Environmental — drainage | Floor drain minimum locations | PT hydrotherapy + 2 soiled utilities + 2 janitor closets (one per floor) | Required locations per program | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.3 Plumbing | Inspection | MEP Engineer of Record (MEP-EOR) / AOR — field verification at rough-in | PT hydrotherapy + soiled utilities + janitor closets | Plumbing / Architecture | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | 5 floor drain locations minimum | GOVERNING | Low | Plumbing | NNN Lease — TI scope | High | Standard clinical plumbing requirement. 5 locations confirmed. | 25 | Low | — | 5 floor drain locations minimum | shall be provided | required locations | — | — | — | N/A
GR-0060 | HHC-SLR-001 | — | Security & Life-Safety Requirements | Access Control | Clinical Entry | Safety | Security — Access Control | Controlled access shall be provided at the clinical suite entry from the shared building lobby on each clinical floor. Card readers or keypads. Integrated with Heritage base building access control system. | Clinical Suite Entry Points | Security — access control | Controlled access at clinical entry | Card reader or keypad at each clinical floor entry / integrated with base building system | All operating hours | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.4 Technology / Low-Voltage | Demonstration | MEP Engineer of Record (MEP-EOR) — access control functional test at commissioning | Clinical entry points, Floors 1 and 2 | Electrical / IT | MEP Engineer of Record (MEP-EOR) | TI scope — infrastructure / Base building — coordination with Heritage system | Access control infrastructure in TI scope; integration with Heritage base building system required | GOVERNING | High | Electrical / IT / Architecture | NNN Lease — TI scope | High | Integration with Heritage base building system requires early coordination with developer's security contractor. | 72 | High | LIFE_SAFETY ¦ MULTI_DISCIPLINE_COORDINATION | card reader or keypad / integrated | shall be provided | all clinical entry points | — | — | — | N/A
GR-0061 | HHC-SLR-002 | GR-0044 | Security & Life-Safety Requirements | Egress | Life Safety | Safety | Life Safety — Egress | AHC occupancy egress shall comply with NFPA 101 Chapter 20. Exit travel distance not exceeding 150 ft. Minimum 2 enclosed exit stairs with IBC §909 pressurization. | Egress — AHC Occupancy | Life safety — egress design | Egress travel distance and stair pressurization | 150 ft max travel / 2 enclosed stairs / IBC §909 pressurization | All clinical areas | Conditional on AHC occupancy confirmation | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-004 / NFPA 101 §20.2.5 / IBC §909 | Analysis + Inspection | AOR — egress travel distance at SD + AHJ final acceptance | Floors 1–2 | Architecture / Fire Protection | Architect of Record (AOR) | Base building scope — egress stairs | Shared egress stairs between clinical and residential occupancies — DF-003 watch item | GOVERNING | Critical | Architecture / Fire Protection | Base building scope — CMAR / A/E Contract | High | DF-003: shared egress stair pressurization not confirmed at SD. Life safety requirement. | 90 | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | 150 ft max / pressurized stairs | shall comply | conditional on AHC confirmation | — | — | — | N/A
GR-0062 | HHC-SLR-003 | — | Security & Life-Safety Requirements | Security | Camera Coverage | Safety | Security — Video Surveillance | Security cameras shall provide coverage of: clinical entry (min 2), primary care waiting (min 2), imaging waiting (min 1), staff corridors (min 4), medication room (1), IT/server room (1). | Security Camera System EQ-074 | Security — video surveillance | Security camera minimum coverage locations | 12 cameras minimum at specified clinical locations | During all operating hours | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.4 Technology | Inspection | MEP Engineer of Record (MEP-EOR) (infrastructure) + Northstar (OFE installation verification) at substantial completion | All clinical areas per coverage plan | Electrical / IT | MEP Engineer of Record (MEP-EOR) (infrastructure) | TI scope — infrastructure / OFE — camera hardware by Northstar | 12-camera minimum coverage; OFE hardware by Northstar; infrastructure (conduit, power, data) in TI scope | GOVERNING | Moderate | Electrical / IT | NNN Lease — TI scope | High | Camera system OFE by Northstar. Infrastructure in TI scope. Coverage plan must be coordinated with floor plan at SD. | 55 | Moderate | LIFE_SAFETY | 12 cameras minimum | shall provide coverage | all specified locations | — | — | — | N/A
GR-0063 | HHC-SLR-004 | GR-0049 | Security & Life-Safety Requirements | MRI | Zone Access Control | Safety | Security — MRI Safety | MRI Zone III and Zone IV boundaries shall be controlled access at all times per ACR guidelines. Ferromagnetic screening station (EQ-023) at Zone II/III boundary. | MRI Zone Access Control | Life safety — MRI safety | MRI zone access control | Controlled access Zone III and IV / ferromagnetic screening at Zone II/III boundary | All MRI operations | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-014 / ACR MRI Safety | Inspection + Demonstration | AOR + MEP-EOR — access control and ferromagnetic screening verified at commissioning | MRI Suite, Floor 2 | Architecture / Electrical / Safety | Architect of Record (AOR) | TI scope — Northstar | Zone diagram must appear in CDs; access control per GR-0060 scope | GOVERNING | High | Architecture / Electrical / Safety | NNN Lease — TI scope | High | Projectile risk in MRI zone — life safety requirement. Zone diagram is mandatory in CDs. | 92 | High | LIFE_SAFETY ¦ REGULATORY_APPROVAL | Zone III and IV controlled access | shall be controlled | all MRI operations | — | — | — | N/A
GR-0064 | HHC-SLR-005 | — | Security & Life-Safety Requirements | Workplace Violence | Prevention | Safety | Security — Workplace Violence | Facility design shall support annual worksite analysis for workplace violence prevention per TJC. Controlled entry, unobstructed reception sightlines, and staff duress alarm infrastructure required. | Workplace Violence Prevention — Facility Design | Safety — workplace violence prevention | Facility design support for WPV prevention | Controlled entry + unobstructed sightlines + duress alarm infrastructure | All operating conditions | None | Standard | Northstar TJC Regulatory Requirements Summary v1.0 | RQ-024 / TJC AHC EC Chapter | Inspection | AOR — design review with Northstar security at 60% DD | All clinical areas | Architecture / Electrical | Architect of Record (AOR) | TI scope — Northstar | Duress alarm infrastructure (conduit, low-voltage rough-in) in TI scope; hardware OFE by Northstar | GOVERNING | Moderate | Architecture / Electrical | NNN Lease — TI scope | High | TJC accreditation requirement. Annual worksite analysis requires defensible facility design baseline. | 58 | Moderate | LIFE_SAFETY ¦ REGULATORY_APPROVAL | controlled entry + sightlines + duress alarm | shall support WPV prevention | all operating conditions | — | — | — | N/A
GR-0065 | HHC-OMR-001 | GR-0012 | Operational & Maintenance Requirements | MRI Operations | 24/7 Cooling | Operational | Mechanical — MRI Maintenance | MRI equipment room shall have dedicated precision cooling providing 24/7 capability independent of building HVAC. Critical failure alarm to MRI console and BAS. Temperature continuously logged. | MRI Equipment Room Cooling | Operational — MRI continuity | 24/7 precision cooling for MRI equipment room | 24/7 dedicated cooling / critical failure alarm / continuous temperature logging | Year-round, 24/7 | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-075 Equipment Schedule | Test | MEP Engineer of Record (MEP-EOR) — 24/7 operation verification and alarm test at commissioning | MRI Equipment Room | Mechanical / Controls | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | Non-ferrous cooling unit within 20-gauss line; BAS integration required | GOVERNING | High | Mechanical / Controls | NNN Lease — TI scope | High | 24/7 cooling failure = MRI shutdown. Critical alarm required. Non-ferrous components required within magnet field. | 88 | High | LIFE_SAFETY ¦ HIGH_COST_INFRASTRUCTURE | 24/7 dedicated cooling / critical alarm | shall have | 24/7 year-round | — | — | — | N/A
GR-0066 | HHC-OMR-002 | — | Operational & Maintenance Requirements | IT Operations | Server Room Cooling | Operational | Mechanical — IT Continuity | IT/server room (PACS server and network core) shall have 24/7 dedicated cooling independent of building HVAC. No overhead water lines in server room. | IT Server Room Cooling | Operational — IT continuity | 24/7 dedicated cooling for server room | 24/7 dedicated precision cooling / no overhead water lines | Year-round, 24/7 | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §D Shared Support / EQ-060–061 | Test | MEP Engineer of Record (MEP-EOR) — 24/7 operation verification at commissioning | IT Server Room | Mechanical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar | Liebert or equivalent precision cooling unit; dedicated from building HVAC | GOVERNING | High | Mechanical | NNN Lease — TI scope | High | No overhead water lines = critical infrastructure protection standard. PACS and network core are clinical operations dependencies. | 72 | High | HIGH_COST_INFRASTRUCTURE ¦ LIFE_SAFETY | 24/7 cooling / no overhead water lines | shall have | 24/7 year-round | — | — | — | N/A
GR-0067 | HHC-OMR-003 | GR-0056 | Operational & Maintenance Requirements | Electrical | ATS Maintenance | Operational | Electrical — EES Maintenance | Clinical tenant ATS shall be separate from residential ATS. ATS shall have test provisions accessible without de-energizing clinical EES. Located in tenant electrical room Level 1. | Clinical ATS EQ-063 | Operational — EES maintainability | Clinical ATS isolation and test provisions | Separate from residential ATS / test provisions accessible / Level 1 tenant electrical room | All operating conditions | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-063 Equipment Schedule | Test + Inspection | MEP Engineer of Record (MEP-EOR) — ATS transfer time test + field inspection at commissioning | Tenant Electrical Room, Level 1 | Electrical | MEP Engineer of Record (MEP-EOR) | TI scope — Northstar (ATS) / Base building — electrical room | ATS must be sized for 350kW generator per BCR-003 resolution | GOVERNING | High | Electrical | NNN Lease — TI scope | High | Conditional on BCR-003 generator resolution. Test provisions required so NFPA 99 monthly ATS tests can be performed without clinical disruption. | 68 | High | HIGH_COST_INFRASTRUCTURE ¦ LIFE_SAFETY | separate ATS / test provisions | shall be separate | Level 1 tenant electrical room | — | — | — | N/A
GR-0068 | HHC-OMR-004 | — | Operational & Maintenance Requirements | IT | PACS Infrastructure | Operational | IT — PACS | PACS base infrastructure (conduit, fiber backbone, junction boxes) shall be installed by contractor as TI scope. PACS server hardware and reading workstations are OFE by Northstar. | PACS Infrastructure EQ-027 | Operational — clinical imaging IT | PACS base infrastructure in TI scope | Conduit, fiber backbone, junction boxes as TI scope / PACS hardware as OFE | Clinical imaging spaces and reading suite | None | OFEDoc | Northstar Clinic Equipment Schedule v1.0 | EQ-027 / EQ-028 Equipment Schedule | Inspection | MEP Engineer of Record (MEP-EOR) — infrastructure at rough-in; Northstar IT (OFE installation verification) | Imaging Suite + Reading Suite + IT Server Room | IT / Electrical | MEP Engineer of Record (MEP-EOR) (infrastructure) | TI scope — infrastructure / OFE — PACS hardware by Northstar | Infrastructure (TI scope) must be installed per Northstar IT/PACS vendor rough-in requirements before OFE delivery | GOVERNING | Moderate | IT / Electrical | NNN Lease — TI scope / OFE boundary | High | PACS infrastructure is TI scope; PACS hardware is OFE. Coordinate infrastructure design with Northstar IT and PACS vendor before 50% CD. | 55 | Moderate | MULTI_DISCIPLINE_COORDINATION | conduit + fiber as TI scope | shall be installed | Imaging and reading suite | — | — | — | N/A
GR-0069 | HHC-OMR-005 | — | Operational & Maintenance Requirements | Maintenance Access | Equipment Clearance | Operational | Architecture — Maintainability | All filter racks, fan coil units, VAV terminals, and plumbing cleanouts in the clinical component shall be accessible from walkable surfaces without ladders or scaffolding. Minimum 36-in. clearance at all maintainable MEP equipment. | Clinical MEP Equipment — Maintenance Access | Operational — maintainability | Maintenance accessibility standard | Accessible from walkable surfaces / 36-in. clearance minimum at all MEP equipment | All clinical MEP equipment | None | OwnerCriteria | Heritage Health Campus Owner Program Criteria Rev. 2 | §4.1 HVAC | Inspection | Architect of Record (AOR) — 60% DD coordination review and field verification at substantial completion | All clinical MEP equipment locations | Architecture / Mechanical | Architect of Record (AOR) | TI scope — Northstar | Maintenance access coordination required at DD before MEP ceiling layout is locked | GOVERNING | Moderate | Architecture / Mechanical | NNN Lease — TI scope | High | Gallant OMR standard. Failure to provide accessible maintenance routes creates long-term operating cost and JCAHO compliance risk. | 48 | Moderate | MULTI_DISCIPLINE_COORDINATION | 36-in. clearance / walkable surfaces | shall be accessible | all clinical MEP equipment | — | — | — | N/A
GR-0070 | HHC-OMR-006 | — | Operational & Maintenance Requirements | Closeout | O&M Delivery | Operational | Project Closeout | O&M manuals, as-built drawings, and equipment warranties shall be delivered to Northstar facilities management no later than 30 calendar days after project substantial completion. | O&M Package — Closeout | Operational — facility turnover | O&M package delivery deadline | Delivered within 30 calendar days of substantial completion | Project closeout phase | None | ProgramDoc | Heritage Health Campus Programming Document v1.0 | §G Programming Doc Milestone Schedule | Inspection | Owner's Rep — O&M delivery confirmation within 30 days of substantial completion | Project closeout | Architecture / CMAR | Architect of Record (AOR) + CMAR (Cornerstone Construction) | A/E Contract + CMAR Contract scope | O&M manuals organized by MasterFormat CSI division | GOVERNING | Low | Program Management | A/E Contract + CMAR Contract | High | Standard closeout deliverable. TJC accreditation survey may require O&M manuals and training completion documentation. | 28 | Low | — | 30-day delivery deadline | shall be delivered | within 30 days of substantial completion | — | — | — | N/A
GR-0071 | HHC-RCR-020 | GR-0042 | Regulatory & Compliance Requirements | NMCBC | Governing Standard | Regulatory | Code — AHJ Adopted | All commercial construction within the City of Albuquerque jurisdiction shall comply with the 2021 New Mexico Commercial Building Code (NMCBC / 14.7.2 NMAC), which adopts by reference the 2021 International Building Code with New Mexico amendments. NMCBC is effective July 19, 2023 and is administered by the NM Regulation and Licensing Department, Construction Industries Division (CID). | Commercial Building — All | Regulatory compliance — governing AHJ-adopted code | NMCBC 2021 (14.7.2 NMAC) with NM amendments | Effective July 19, 2023 | New construction on or after July 19, 2023 | None | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2.8 NMAC / §1 Scope | Inspection | AHJ (City of Albuquerque / NM CID) — building permit issuance and final inspection | All building occupancies — Heritage Health Campus | Architecture / All disciplines | City of Albuquerque / NM CID | Base building scope — Heritage / TI scope — Northstar | Governs all base building code compliance requirements including occupancy, construction type, egress, fire protection, and accessibility | GOVERNING | High | Architecture / All Disciplines | A/E Contract — code compliance basis | High | SUPPLEMENT to GR-0042 (TJC AHC accreditation) and GR-0019 (IBC compliance). Confirms base code as NMCBC not standalone IBC. Partially informs DF-NEW-001 — commercial base code is confirmed; FGI edition remains NM DOH jurisdiction. | 82 | High | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | shall comply | shall comply | all commercial construction |  |  |  | N/A
GR-0072 | HHC-SER-004 | GR-0057 | Sustainability & Environmental Requirements | Energy | NMCECC | Sustainability | Code — Energy (NM) | The energy conservation aspects of the Heritage Health Campus commercial construction shall comply with the New Mexico Commercial Energy Conservation Code (NMCECC / 14.7.6 NMAC), applied in conjunction with the NMCBC. The NMCECC governs energy conservation for general commercial construction in New Mexico and takes precedence over standalone ASHRAE 90.1-2019 references where NM amendments apply. | Building Energy Performance — All Occupancies | Sustainability — NM energy code compliance | NMCECC (14.7.6 NMAC) compliance | Applied concurrently with NMCBC (14.7.2 NMAC) | All design phases | NM-specific amendments may modify ASHRAE 90.1 provisions | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2.8 NMAC §13 / 14.7.6 NMAC | Analysis | MEP Engineer of Record (MEP-EOR) — NMCECC compliance report at 90% CD demonstrating compliance with NM-specific energy provisions | All building occupancies | Mechanical / Electrical | MEP Engineer of Record (MEP-EOR) | Base building and TI scope | NMCECC is the NM AHJ-adopted energy code. GR-0057 (SER-001) references ASHRAE 90.1-2019 — NMCECC may include NM-specific amendments that modify the standalone standard. | GOVERNING | Moderate | Mechanical / Electrical | A/E Contract — code compliance | High | SUPPLEMENT to GR-0057 (SER-001 ASHRAE 90.1). NMCECC is the AHJ-confirmed governing energy standard for NM. Energy compliance report at 90% CD must reference NMCECC, not standalone ASHRAE 90.1. | 50 | Moderate | REGULATORY_APPROVAL | shall comply with NMCECC | shall apply | all commercial construction |  |  |  | N/A
GR-0073 | HHC-PIR-012 | GR-0061 | Physical & Interface Requirements | Circulation | Stairway Dimensions | Physical | Architecture — Stairways | Exit stair and exit access stair construction shall comply with NMCBC Chapter 10 dimensional requirements: riser height minimum 4 inches (102mm), maximum 7 inches (178mm); tread depth minimum 11 inches (279mm). Handrail height minimum 34 inches, maximum 38 inches above stair nosing. Landings required at all floor levels. | Exit Stairs and Stair Dimensions | Physical dimensional compliance | Stair riser: 4" min / 7" max; tread: 11" min; handrail: 34"–38" | Per NMCBC Table — riser 4"–7" / tread ≥11" | All stairway construction | Stairways within individual dwelling units may comply with alternate residential provisions per NMCBC §1011.5.2 | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC Ch. 10 §1011 / Table | Inspection | Architect of Record (AOR) — dimensional verification at construction documents and field measurement at substantial completion | All exit stairs, exit access stairs — Heritage Health Campus | Architecture | Architect of Record (AOR) | Base building scope — egress stairs / TI scope — any internal clinical stairs | NMCBC-specific stairway dimensions govern. Residential dwelling unit stairways may use alternate provisions under §1011.5.2. | GOVERNING | Moderate | Architecture | A/E Contract — code compliance | High | SUPPLEMENT to GR-0061 (SLR-002 egress). Adds specific NM dimensional requirements for stair construction. Design team must confirm stair design against NMCBC Chapter 10 Table at SD. DF-003: shared egress stairs between clinical and residential — confirm dimensional compliance for both occupancy types. | 52 | Moderate | REGULATORY_APPROVAL | 4" min / 7" max riser; 11" min tread | shall comply | all exit stairways |  |  |  | N/A
GR-0074 | HHC-RCR-021 | — | Regulatory & Compliance Requirements | ADA/NM | Baby Changing Facilities | Regulatory | Code — NM Specific | Construction of a new restroom intended for use in a place of public accommodation shall provide for at least one baby changing facility on each floor that has a public toilet facility, accommodating any person needing to utilize a baby changing facility, pursuant to Section 50-13-10.5 NMSA 1978 and NMCBC. | Baby Changing Facilities — All Public Toilet Floors | Regulatory compliance — NM-specific accessibility requirement | Minimum 1 baby changing facility per floor with public toilet facility | Each floor containing a public restroom | New construction with public accommodation use | None | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC §16 / NMSA §50-13-10.5 | Inspection | Architect of Record (AOR) — fixture schedule and floor plan verification at SD; field verification at substantial completion | All floors with public toilet facilities — Floors 1–2 (clinical) and lobby | Architecture | Architect of Record (AOR) | TI scope — Northstar (clinical floors) / Base building — lobby/common areas | NM-specific requirement with no direct equivalent in IBC or ADA 2010 Standards. Required in all public accommodation restrooms. Applies to clinical floors and common area restrooms. Must appear in fixture schedule. | GOVERNING | Moderate | Architecture | NNN Lease — TI scope (clinical) / Base building (common) | High | NEW requirement — not in any prior source document. NM-specific statutory requirement per NMSA 50-13-10.5. Clinical floors 1–2 are public accommodation. Baby changing station must appear in SD fixture schedule. | 48 | Moderate | REGULATORY_APPROVAL | at least one per floor with public toilet | shall provide | all floors with public toilet facilities |  |  |  | N/A
GR-0075 | HHC-PIR-013 | — | Physical & Interface Requirements | Building Height | NMCBC Table 504 | Physical | Structural — Building Height | The 7-story Heritage Health Campus building shall be confirmed as compliant with NMCBC Table 504 maximum allowable height and number of stories for the applicable construction type (Type IA) and occupancy group(s). Type IA construction with sprinklers is confirmed to permit unlimited height per NMCBC Table 504. | Building Height — 7 Stories | Physical — building height code compliance | 7 stories above grade — within Type IA unlimited height per NMCBC Table 504 | All phases | Type IA construction with NFPA 13 full sprinkler protection throughout | Mixed occupancies (AHC clinical + residential Group R-2) must each be verified independently | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC Ch. 5 §504 / Table 504 | Analysis | Architect of Record (AOR) — code compliance matrix at SD confirming Table 504 compliance for each occupancy group | All building floors — Floors 1–7 | Architecture / Structural | Architect of Record (AOR) | Base building scope — Heritage | Type IA (sprinklered) is confirmed to have no height limit per IBC/NMCBC Table 504. Mixed occupancy verification required for Group B/I-2 (clinical) and Group R-2 (residential). AHC occupancy classification pending per GR-0044. | GOVERNING | Moderate | Architecture / Structural | A/E Contract — code compliance | High | NEW requirement added from NMCBC source. Type IA unlimited height confirmed. Code compliance matrix at SD must show Table 504 verification for each occupancy group. Note: AHC occupancy (GR-0044) must be confirmed before code compliance matrix is finalized. | 45 | Moderate | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | 7 stories / Type IA unlimited | shall comply with Table 504 | all occupancy groups |  |  |  | N/A
GR-0076 | HHC-RCR-022 | GR-0047 | Regulatory & Compliance Requirements | Construction Type | Type IA Non-Combustible | Regulatory | Code — Construction Type | Heritage Health Campus shall be constructed as Type IA (unprotected non-combustible) construction per NMCBC Chapter 6. All structural members, exterior walls, and fire resistance-rated assemblies shall comply with Type IA construction requirements. Stairways within individual dwelling units (Floors 3–7) are permitted to be of combustible construction per NMCBC Chapter 10 NM amendment. | Building Construction Type — Type IA | Regulatory compliance — construction type requirements | Type IA — non-combustible throughout / combustible exception for residential unit stairways | All construction phases | None | NM amendment permits combustible stairways within individual dwelling units per Chapter 10 | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC Ch. 6 §602 | Inspection | AHJ (NM CID / Albuquerque Building Dept) — construction type verified at permit review and field inspection | All building floors — Heritage Health Campus | Architecture / Structural | Architect of Record (AOR) + Structural Engineer of Record (SER) | Base building scope — Heritage | Type IA confirmed in Programming Document and OPC. NMCBC Ch. 6 confirms requirements. NM amendment: combustible stairways permitted within individual dwelling units only — clinical stairways must remain non-combustible. | GOVERNING | Moderate | Architecture / Structural / Fire Protection | A/E Contract — code compliance | High | SUPPLEMENT to GR-0047 (NFPA 13 sprinkler). Confirms Type IA construction basis. NM amendment on combustible residential stairways noted — does not affect clinical floors. Coordinate with structural engineer: post-tensioned concrete slab is non-combustible by default. | 48 | Moderate | REGULATORY_APPROVAL | Type IA non-combustible | shall be constructed | all structural and rated assemblies |  |  |  | N/A
GR-0077 | HHC-PIR-014 | GR-0054 | Physical & Interface Requirements | Accessible Parking | Van-Accessible Spaces | Physical | Site — Accessible Parking | The Heritage Health Campus parking facility shall provide accessible parking spaces including van-accessible spaces per NMCBC Chapter 11 and ADA 2010 Standards. Accessible spaces shall be located on the shortest accessible route to the clinical building entrance. | Accessible Parking — Site | Physical — accessible parking layout | Van-accessible spaces required per NMCBC Table 11 / ADA 2010 Standards ratio | At building entrance and parking structure | None | Parking structure is a separate contract per Programming Document — accessible route coordination required | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC Ch. 11 §1106 | Inspection | Architect of Record (AOR) / Civil Engineer — site plan compliance verification at SD; field verification at substantial completion | Parking structure / Site — Heritage Health Campus | Architecture / Civil | Civil Engineer + Architect of Record (AOR) | Separate parking structure contract — base building coordination | Parking structure is a separate contract per Programming Document. A/E must coordinate accessible route from parking to clinical building entrance. Van-accessible spaces on shortest route to building entry. | GOVERNING | Moderate | Architecture / Civil | Separate parking structure contract / Base building coordination | High | SUPPLEMENT to GR-0054 (ADA accessibility). Adds NM/NMCBC parking-specific requirements. Parking structure is per Programming Document a separate contract — accessible route coordination must be confirmed at SD. | 45 | Moderate | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | van-accessible spaces required | shall provide | parking facility |  |  |  | N/A
GR-0078 | HHC-RCR-023 | — | Regulatory & Compliance Requirements | Mechanical/Plumbing | NM Trade Codes | Regulatory | Code — NM Trade Codes | Mechanical systems shall comply with the New Mexico Mechanical Code (NMMC). Plumbing systems shall comply with the New Mexico Plumbing Code (NMPC). All NMCBC references to the International Mechanical Code (IMC) and International Plumbing Code (IPC) are replaced by the NMMC and NMPC respectively. | Mechanical and Plumbing Systems — All | Regulatory compliance — NM trade code substitution | NMMC (mechanical) + NMPC (plumbing) replace IMC + IPC | Design through construction | None | Medical gas systems remain under NFPA 99 per GR-0045 | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC §1 / NM code adoption provisions | Inspection | MEP Engineer of Record (MEP-EOR) — verify NM code compliance in CD specifications; AHJ mechanical and plumbing permit review | All mechanical and plumbing systems — Heritage Health Campus | Mechanical / Plumbing | MEP Engineer of Record (MEP-EOR) | Base building and TI scope | NMMC and NMPC are NM state adoptions. A/E specifications must reference NMMC/NMPC, not IMC/IPC. Medical gas systems are separately governed by NFPA 99 (GR-0045) and are not affected by this substitution. | GOVERNING | Moderate | Mechanical / Plumbing | A/E Contract — code compliance | High | NEW requirement — not explicitly referenced in prior source documents. Critical for A/E specification writing: CD specs must cite NMMC/NMPC, not IMC/IPC. MEP Engineer of Record (MEP-EOR) to confirm NMMC/NMPC adoption basis at 50% SD MEP narratives. | 48 | Moderate | REGULATORY_APPROVAL | NMMC/NMPC govern | shall comply | all mechanical and plumbing systems |  |  |  | N/A
GR-0079 | HHC-PIR-015 | GR-0040 | Physical & Interface Requirements | Structural | Concrete Standards | Physical | Structural — Concrete | Concrete construction for Heritage Health Campus shall comply with ACI 318 as adopted and referenced in NMCBC Chapter 19. Concrete mixing, curing, and material specifications shall comply with ACI 318 requirements confirmed under the NM governing code basis. | Concrete Construction — Post-Tensioned Slab and Foundation | Physical structural design — concrete standard | ACI 318 compliance for all concrete construction | Design through construction | None | Post-tensioned flat plate is ACI 318 governing system | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC Ch. 19 §1901 | Analysis | Structural Engineer of Record (SER) — structural calculations reference ACI 318 at 30% DD; field inspection of concrete mix design and curing records during construction | All concrete structural elements | Structural | Structural Engineer of Record (SER) | Base building scope — Heritage | ACI 318 confirmed as governing concrete standard under NMCBC. Post-tensioned flat plate slab (base building structural system) must be designed per ACI 318. Concrete mix design and curing records required. | GOVERNING | Moderate | Structural | A/E Contract / CMAR Contract — structural and concrete scope | High | SUPPLEMENT to GR-0040 (PIR-010 PT hydrotherapy slab). Confirms ACI 318 as governing concrete standard for all concrete elements including post-tensioned flat plate. Structural calculations at 30% DD must reference ACI 318. | 42 | Low | MULTI_DISCIPLINE_COORDINATION | ACI 318 compliance | shall comply | all concrete construction |  |  |  | N/A
GR-0080 | HHC-SLR-006 | GR-0061 | Security & Life-Safety Requirements | Stairways | Construction Materials | Safety | Life Safety — Stair Construction | Exit stairs and exit access stairs serving the clinical occupancy (Floors 1–2) and mixed-occupancy egress shall be of non-combustible construction. NM amendment under NMCBC Chapter 10 permits combustible stairways only within individual dwelling units — this exception does not apply to the shared egress stairs serving clinical and residential occupancies. | Exit Stair Construction Materials — Clinical and Shared Egress | Life safety — stair construction material | Non-combustible exit stairs required for clinical and shared egress | All exit stairs serving mixed occupancy | None | NM amendment permits combustible stairways within individual dwelling units only per NMCBC §1011 | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | 14.7.2 NMAC — NMCBC Ch. 10 §1011 NM amendment | Inspection | Architect of Record (AOR) — construction type verified at CD specifications and field inspection | All exit stairs — Heritage Health Campus | Architecture / Structural | Architect of Record (AOR) | Base building scope — Heritage | DF-003: shared egress stairs between clinical and residential occupancies. NM amendment does NOT apply to shared stairs — these must be non-combustible. Residential unit internal stairs may be combustible but are not the means of egress for this building. | GOVERNING | Moderate | Architecture / Structural / Fire Protection | Base building scope — A/E Contract | High | SUPPLEMENT to GR-0061 (SLR-002 egress). Clarifies that NM combustible stair exception is limited to individual dwelling unit interior stairs only. Shared egress stairs must be non-combustible. DF-003 stair pressurization issue remains open. | 55 | Moderate | LIFE_SAFETY ¦ REGULATORY_APPROVAL | non-combustible exit stairs required | shall be non-combustible | clinical and shared egress stairs |  |  |  | N/A
GR-0081 | HHC-PIR-016 | GR-0032 | Physical & Interface Requirements | Space Program | Exam Room NSF — NM Amendment | Physical | Space Program — NM DOH | Standard exam rooms shall provide minimum 120 NSF clear floor area exclusive of toilet rooms and fixed casework, per NM DOH Amendment NM-004 to FGI 2022. This supersedes the FGI 2022 standard of 100 NSF for all 12 standard exam rooms in the Northstar clinic. | Exam Rooms — Standard (12 of 16) | Space program compliance — NM-specific | Exam room minimum clear floor area — NM Amendment NM-004 | 120 NSF minimum clear | All 12 standard exam rooms | Exclusive of toilet rooms and fixed casework; 4 accessible exam rooms at 140 NSF per GR-0032 unaffected | Code | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | NM DOH Amendment NM-004 / AHJ Pre-Application Response June 3, 2025 | Inspection | Architect of Record (AOR) — dimension verification at SD floor plan and field measurement | All 12 standard exam rooms | Architecture | Architect of Record (AOR) | TI scope — Northstar | NM Amendment NM-004 increases exam room standard from 100 NSF to 120 NSF. This requirement supersedes GR-0032 (PIR-002) for standard exam rooms. SD floor plan revision required before SD gate approval. | GOVERNING | Critical | Architecture | NNN Lease — TI scope | High | SUPERSEDES GR-0032 for 12 standard exam rooms. Design revision required at SD — all standard exam rooms must increase from 100 NSF to 120 NSF minimum. 4 accessible exam rooms at 140 NSF remain as GR-0032. New source: NM DOH Pre-Application Response (Doc 9). | 88 | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | 120 NSF minimum | shall provide | 12 standard exam rooms |  |  |  | N/A
GR-0082 | HHC-SMR-011 | — | Schedule & Milestone Requirements | A/E Procurement | NM Licensure | Schedule | Procurement — A/E Qualification | The Architect of Record shall be licensed to practice architecture in the State of New Mexico prior to A/E NTP. All required engineering subconsultants (structural, mechanical, plumbing, electrical, fire protection, civil) shall be licensed in New Mexico prior to executing their respective subconsultant agreements. | A/E Team — NM Professional Licensure | Procurement — professional qualification | NM professional licensure for all required engineering disciplines | Licensed in New Mexico prior to NTP | A/E NTP and throughout the engagement | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §V Required Disciplines / §VIII.A Contract Form | Inspection | Owner's Rep — verification of NM license numbers at contract execution; A/E provides license certificate in proposal Tab 1 | A/E NTP | Architecture / All Engineering | Owner's Rep — Owner's PM | A/E Contract scope | NM licensure is a threshold qualification requirement. A/E team confirmed licensed in NM per kickoff meeting attendance. | GOVERNING | Low | Program Management | A/E Contract — professional qualification | High | Architect of Record (AOR) + Interiors confirmed NM licensed. Southwest MEP Engineers and Structural Engineer of Record (SER) confirmed NM licensed per kickoff meeting record. | 22 | Low | REGULATORY_APPROVAL | licensed in New Mexico | shall be licensed | A/E NTP and throughout |  |  |  | N/A
GR-0083 | HHC-OMR-007 | — | Operational & Maintenance Requirements | A/E Performance | Professional Liability Insurance | Operational | A/E Contract — Insurance | The A/E shall maintain Professional Liability (Errors and Omissions) insurance of $2,000,000 per occurrence / $4,000,000 aggregate, maintained for a minimum of 3 years post-project completion. | A/E Professional Liability Insurance | A/E contract risk management | E&O insurance minimum | $2M per occurrence / $4M aggregate / 3-year post-completion | Throughout A/E engagement and 3 years after project completion | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §VIII.B Insurance Requirements | Inspection | Owner's Rep — certificate of insurance at contract execution and annually thereafter | A/E Contract duration + 3 years | Program Management | Owner's Rep — Owner's PM | A/E Contract scope | Insurance requirement protects Owner from A/E design errors and omissions. Certificate of insurance required at contract execution. | GOVERNING | Low | Program Management | A/E Contract — §VIII.B | High | Standard commercial A/E insurance requirement. Certificate provided by AOR at contract execution. | 18 | Low | — | $2M/$4M E&O / 3 years post-completion | shall maintain | A/E engagement and 3 years post-completion |  |  |  | N/A
GR-0084 | HHC-OMR-008 | GR-0069 | Operational & Maintenance Requirements | A/E Performance | Submittal Review Turnaround | Operational | A/E Contract — Performance Standards | The A/E shall complete review of all contractor submittals within 14 calendar days of receipt of a complete submittal. Incomplete submittals may be returned without review. | Contractor Submittals — A/E Review | A/E performance standard — submittal review | Submittal review turnaround time | 14 calendar days maximum from receipt of complete submittal | Construction administration phase | Incomplete submittals may be returned without review | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §VIII.C Performance Standards | Test | Owner's Rep — monitor submittal log for compliance with 14-day review cycle | Construction administration phase | Architecture / All Engineering | Architect of Record (AOR) | A/E Contract scope | 14-day maximum is a contractual performance standard. Compliance monitored via CMAR submittal log in Procore. | GOVERNING | Moderate | Program Management | A/E Contract — §VIII.C | High | Performance standard binding on A/E. Critical for clinical equipment submittals with vendor lead times. Delays in submittal review cascade to long-lead procurement. | 45 | Moderate | MULTI_DISCIPLINE_COORDINATION | 14 calendar days maximum | shall complete review | construction administration phase |  |  |  | N/A
GR-0085 | HHC-OMR-009 | — | Operational & Maintenance Requirements | A/E Performance | RFI Response Turnaround | Operational | A/E Contract — Performance Standards | The A/E shall provide written response to all contractor RFIs within 10 calendar days of receipt. | Contractor RFIs — A/E Response | A/E performance standard — RFI response | RFI response turnaround time | 10 calendar days maximum from receipt | Construction administration phase | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §VIII.C Performance Standards | Test | CMAR — monitor RFI log for compliance; report to Owner if A/E misses response window | Construction administration phase | Architecture / All Engineering | Architect of Record (AOR) | A/E Contract scope | 10-day RFI response is a contractual standard. Overdue RFIs are a schedule risk, particularly for clinical systems. | GOVERNING | Moderate | Program Management | A/E Contract — §VIII.C | High | CMAR (Cornerstone Construction) to monitor RFI log. Any RFI overdue by more than 3 days to be flagged to Owner's Rep. | 42 | Moderate | MULTI_DISCIPLINE_COORDINATION | 10 calendar days maximum | shall provide | construction phase |  |  |  | N/A
GR-0086 | HHC-OMR-010 | — | Operational & Maintenance Requirements | A/E Performance | Gallant RIR Conflict Response | Operational | A/E Contract — Gallant Coordination | The A/E shall respond in writing to all Gallant Requirements Intelligence™ RIR conflict items and DECISION-PENDING items within 10 Business Days of receipt. Response shall be a written disposition: accept, reject with rationale, or propose alternative resolution. | Gallant RIR Conflict Items — A/E Response | A/E contract obligation — requirements management | RIR conflict item response deadline | 10 Business Days maximum from receipt | All design phases with active RIR cycles | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §II.A Gallant Coordination / §VIII.C Performance Standards | Inspection | Gallant Project Solutions LLC — track response dates in register event ledger | All design phases | Architecture / All Engineering | Architect of Record (AOR) | A/E Contract scope | This is the most operationally significant A/E performance standard from the RFP. Unanswered RIR conflict items block phase gate approval. | GOVERNING | High | Program Management / All Disciplines | A/E Contract — mandatory condition | High | Per RFP §II.A: this is a condition of the A/E contract, not advisory. Gallant tracks response dates in the event ledger. Overdue responses are escalated to Owner at phase gate reviews. | 68 | High | DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | 10 Business Days maximum | shall respond in writing | all design phases |  |  |  | N/A
GR-0087 | HHC-OMR-011 | — | Operational & Maintenance Requirements | A/E Performance | Site Observation Reports | Operational | A/E Contract — CA Performance | The A/E shall issue site observation reports within 3 Business Days of each site visit during the construction administration phase. | Site Observation Reports — CA Phase | A/E performance standard — CA reporting | Site observation report turnaround | 3 Business Days maximum from site visit | Construction administration phase | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §VI Construction Administration | Inspection | Owner's Rep — monitor CA report log | Construction administration phase | Architecture | Architect of Record (AOR) | A/E Contract scope | 3-Business-Day report turnaround is standard commercial CA practice. Reports document A/E's observations and flag potential compliance issues. | GOVERNING | Low | Program Management | A/E Contract — §VI | High | A/E site visits: biweekly minimum during construction; weekly during critical phases (foundation, structural, MEP rough-in, MRI installation, clinical TI, systems startup). | 22 | Low | — | 3 Business Days maximum | shall issue | construction phase |  |  |  | N/A
GR-0088 | HHC-OMR-012 | GR-0070 | Operational & Maintenance Requirements | Closeout | As-Built Deliverables | Operational | A/E Contract — Closeout | As-built drawings shall be delivered within 30 calendar days of project completion in the following formats: Revit model (native file + IFC export), full-size PDF drawings (all disciplines), and PDF specifications. All as-built documents shall reflect the verified constructed condition. | As-Built Documents — Project Closeout | Project closeout — as-built deliverable standard | As-built format and delivery deadline | Within 30 calendar days of project completion; Revit native + IFC + PDF all disciplines | Project closeout phase | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §VI Construction Administration | Inspection | Owner's Rep — delivery confirmation with date stamp within 30 days of substantial completion | Project closeout | Architecture / All Engineering | Architect of Record (AOR) (lead) | A/E Contract scope | Revit model with IFC export is the standard for healthcare facility owners — enables future renovation BIM. IFC enables owner's CAFM/CMMS integration. | GOVERNING | Moderate | Program Management | A/E Contract — §VI | High | SUPPLEMENT to GR-0070 (OMR-006 O&M delivery). Adds specific Revit model deliverable requirement. GR-0070 covers O&M manuals and warranties; this covers as-built drawings and model. | 45 | Moderate | MULTI_DISCIPLINE_COORDINATION | 30 days / Revit + IFC + PDF | shall be delivered | project closeout |  |  |  | N/A
GR-0089 | HHC-PIR-017 | — | Physical & Interface Requirements | BIM | Clash Detection Reporting | Physical | BIM Coordination | Navisworks clash detection reports shall be produced and transmitted to the Owner at 50% SD, 60% DD, and 90% CD. Critical clashes (MEP/structural/architectural) shall be resolved before each phase gate submittal. The A/E shall maintain a coordination log transmitted to Owner's Rep monthly. | BIM Clash Detection — Required Deliverable | BIM coordination — clash detection standard | Clash detection reports at three phase gates | 50% SD, 60% DD, 90% CD — Navisworks reports required | All design phases with BIM model | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §VII.A.8 Quality Control / AOR BIM Plan | Inspection | Owner's Rep / Gallant — verify clash detection reports in Procore transmittal log at each gate | 50% SD, 60% DD, 90% CD | Architecture / All Engineering | Architect of Record (AOR) (BIM lead) | A/E Contract scope | BIM clash detection at 50% SD was confirmed in the kickoff meeting (AI-003 referenced BIM coordination). The 50% SD run produced the BIM Issues Log (July 11, 2025) with 12 issues including the CF-008 Zone IV penetration. | GOVERNING | High | Architecture / Structural / MEP | A/E Contract — §VII.A.8 | High | First clash detection report delivered July 11, 2025 with the 50% SD package. 12 issues identified including CF-008 (MRI Zone IV boundary penetration — CRITICAL). Coordination log to be maintained monthly. | 65 | High | MULTI_DISCIPLINE_COORDINATION ¦ REGULATORY_APPROVAL | Navisworks clash detection at 3 gates | shall be produced | 50% SD, 60% DD, 90% CD phase gates |  |  |  | N/A
GR-0090 | HHC-PIR-018 | GR-0026 | Physical & Interface Requirements | SD Deliverables | BOD Narrative Content | Physical | Design Deliverable — BOD Standard | The 50% SD Basis of Design narrative shall contain at minimum: (1) occupancy classification and code basis by floor; (2) structural system description with MRI point load basis; (3) HVAC configuration by zone; (4) electrical design basis including EES, generator, and ATS; (5) plumbing design basis including medical gas; (6) all Design Flags (DF); (7) all Design Assumptions (DA); (8) VE watch items; (9) open action items requiring owner decision before SD complete or DD NTP. | Basis of Design Narrative — Minimum Content | Design deliverable standard — BOD content | BOD minimum 9-element content standard | 9 specific elements required per RFP §II.C.2 | 50% SD submission — July 11, 2025 | Live document updated at each phase gate | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §II.C.2 Basis of Design Narrative Requirements | Inspection | Gallant — verify BOD completeness against 9-element checklist at RIR Cycle 1 review | 50% SD gate | Architecture / All Engineering | Architect of Record (AOR) | A/E Contract scope | The BOD is the primary design decision document at 50% SD. Gallant processes the BOD as a source document. Incomplete BOD = incomplete 50% SD deliverable. Gallant will not recommend SD gate approval without a compliant BOD. | GOVERNING | High | Architecture / All Disciplines | A/E Contract — §II.C.2 | High | SUPPLEMENT to GR-0026 (SMR-010 50% SD deliverable). Adds the specific 9-element content standard for the BOD narrative. GR-0026 establishes the submission deadline; this governs the content standard. | 65 | High | MULTI_DISCIPLINE_COORDINATION ¦ DECISION_REQUIRED | 9-element BOD minimum content | shall contain at minimum | 50% SD submission |  |  |  | N/A
GR-0091 | HHC-SMR-012 | — | Schedule & Milestone Requirements | Phase Gates | Payment Contingency on Gallant RIR | Schedule | Phase Gate — Payment Condition | Payment for each design phase shall be contingent on Owner acceptance of that phase's deliverables, which includes satisfactory Gallant Requirements Intelligence™ RIR review. The A/E shall not invoice for a phase until the Owner has issued written acceptance following Gallant gate review. | A/E Phase Payments — Gate Acceptance Condition | Contract — phase payment standard | Phase payment contingency on Owner acceptance + satisfactory Gallant RIR | Applies at 50% SD, SD Gate, 30% DD, 60% CD, and 100% CD | All design phases | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §III Phase Gate Requirements — Gallant RIR Integration | Inspection | Owner's Rep — issue written acceptance letter after Gallant gate review at each milestone | All design phase gates | Program Management | Owner's Rep — Owner's PM | A/E Contract scope | This is the enforcement mechanism for the requirements management process. Phase payment is withheld until Gallant confirms the deliverable meets the register requirements. This creates a direct financial incentive for the A/E to respond to RIR conflict items. | GOVERNING | High | Program Management | A/E Contract — §III | High | This requirement establishes Gallant gate review as a payment condition — not advisory. All five gates (50% SD, SD Gate, 30% DD, 60% CD, 100% CD) require Gallant satisfactory review before Owner issues written acceptance. | 72 | High | DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | satisfactory Gallant RIR review | shall be contingent on | all design phase gates |  |  |  | N/A
GR-0092 | HHC-PIR-019 | GR-0016 | Physical & Interface Requirements | Acoustic | Acoustic Consulting Scope | Physical | Architecture — Acoustic | Acoustic consulting shall be provided as a mandatory A/E subconsultant discipline. Scope shall include: STC 60 / IIC 55 between Level 2 clinical and Level 3 residential; STC 45–50 exam room partition isolation; HIPAA acoustic compliance documentation; telemedicine room acoustic treatment (minimum absorption coefficient 0.20 at 250–2000 Hz); and acoustic overlay at Level 2/3 interface per NM Amendment NM-003. | Acoustic Consulting — Mandatory Scope | A/E subconsultant — acoustic design standard | Mandatory acoustic consulting scope for clinical/residential mixed-use | STC 60/IIC 55 at L2/L3; STC 45-50 exam rooms; HIPAA compliance; telemedicine 0.20 absorption | Design through commissioning | None | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §V Required Disciplines — Acoustic Consulting | Analysis + Test | Acoustic Subconsultant — calculation at DD + field measurement at commissioning | All acoustic separation assemblies | Architecture / Acoustic | Acoustic Subconsultant (mandatory) | TI scope — Northstar | Acoustic subconsultant is mandatory per RFP. This confirms the scope that was open in the baseline register. NM Amendment NM-003 (STC 60/IIC 55 at Level 2/3) confirmed by AHJ pre-application response. | GOVERNING | High | Architecture / Acoustic / Structural | A/E Contract — §V | High | SUPPLEMENT to GR-0016 (PR-008 exam room acoustic) and GR-0050 (RCR-009 STC 60). Acoustic consulting scope now formally defined in A/E contract. CMAR constructability review confirmed acoustic overlay adds 3–4 inches to Level 3 FFL. | 68 | High | REGULATORY_APPROVAL ¦ HIGH_COST_INFRASTRUCTURE ¦ MULTI_DISCIPLINE_COORDINATION | STC 60/45/0.20 mandatory scope | shall be provided | all design phases |  |  |  | N/A
GR-0093 | HHC-PIR-020 | — | Physical & Interface Requirements | AV Infrastructure | AV Rough-In in TI Scope | Physical | IT / Electrical — AV Infrastructure | The A/E shall design and include in the clinical TI construction documents all audio-visual infrastructure required by the Owner's separately-engaged AV vendor: conduit routing, power circuits, and data rough-in. AV hardware is OFE by Northstar. AV vendor input drawings shall be incorporated into the A/E's CDs by 50% CD. | AV Infrastructure — Clinical Spaces | Physical — AV rough-in in TI scope | AV conduit, power, and data rough-in in TI scope | All AV infrastructure required per AV vendor input drawings by 50% CD | 50% CD submittal | AV hardware is Owner-Furnished Equipment (OFE) — A/E designs infrastructure only | ProcurementDoc | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | §IV Services Not in A/E Scope — Audio-Visual Design | Inspection | MEP Engineer of Record (MEP-EOR) — AV infrastructure in 50% CD rough-in drawings; Northstar IT confirms coverage | 50% CD submittal | Electrical / IT | MEP Engineer of Record (MEP-EOR) (infrastructure) | TI scope — infrastructure / OFE — AV hardware by Northstar | AV vendor not yet engaged at RFP issuance. A/E to design infrastructure per AV vendor input once AV vendor is engaged by Northstar. Coordinate with PACS infrastructure (GR-0068). | GOVERNING | Moderate | Electrical / IT | NNN Lease — TI scope | High | NEW requirement. AV infrastructure is TI scope; AV hardware is OFE. A/E cannot finalize AV rough-in until Northstar engages AV vendor and provides input drawings. AV vendor engagement is a 50% CD dependency. | 45 | Moderate | MULTI_DISCIPLINE_COORDINATION | AV infrastructure by 50% CD | shall design and include | 50% CD submittal |  |  |  | N/A
GR-0094 | HHC-SMR-013 | GR-0026 | Schedule & Milestone Requirements | Design Workflow | Procore Platform | Schedule | Program Management — Workflow | All design submittals shall be transmitted via the Procore project management platform. Heritage PM will issue Procore access credentials to all project team members by May 16, 2025. All submittals shall include a cover sheet identifying: document title, version, date, transmittal reference, and list of open items requiring Owner response. | Procore Submittal Platform | Design workflow — submittal transmission platform | Procore as mandatory submittal transmission platform | All submittals via Procore | All design phases from SD through CA | Gallant has 14 calendar days post-receipt for source document processing per kickoff protocol | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §6.1 Document Submission and Review | Inspection | Owner's Rep — confirm Procore transmittal log is current at each phase gate review | All design phases | Program Management | Owner's Rep — Owner's PM | A/E Contract scope / Owner-issued platform | Procore selected as project management platform at kickoff. Credentials issued May 16, 2025. All phase-gate submittals and RFIs flow through Procore. | GOVERNING | Low | Program Management | A/E Contract / Owner-issued platform | High | SUPPLEMENT to GR-0026 (50% SD submission). Procore is the confirmed submittal transmission mechanism for all deliverables. BIM 360 access for SER and Southwest MEP also confirmed. | 18 | Low | MULTI_DISCIPLINE_COORDINATION | via Procore platform | shall be transmitted | all design phases |  |  |  | N/A
GR-0095 | HHC-PIR-021 | GR-0041 | Physical & Interface Requirements | BIM Coordination | OFE Revit Tagging | Physical | BIM — OFE Integration | All OFE items from the Northstar Clinic Equipment Schedule v1.0 shall be modeled in Revit by 30% DD based on vendor-confirmed dimensions. OFE equipment families shall be clearly tagged with EQ-ID numbers from the Equipment Schedule. | OFE Equipment — Revit Model | BIM coordination — OFE integration standard | All 56 Equipment Schedule OFE items modeled in Revit with EQ-IDs by 30% DD | 30% DD (October 31, 2025) | All OFE items in Equipment Schedule v1.0 | Based on vendor-confirmed dimensions — MRI model confirmation (GR-0018) required before EQ-020 can be modeled | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §6.2 BIM and Drawing Coordination | Inspection | Owner's Rep / Gallant — verify OFE families with EQ-IDs present in Revit model at 30% DD clash detection run | 30% DD gate | Architecture | Architect of Record (AOR) (BIM lead) | A/E Contract scope | SUPPLEMENT to GR-0041 (PIR-011 OFE integration). Adds specific Revit modeling standard with EQ-ID tagging. BIM 360 access confirmed for Structural Engineer of Record (SER) and Southwest MEP Engineers. | GOVERNING | Moderate | Architecture / All Engineering | A/E Contract / BIM Execution Plan | High | SUPPLEMENT to GR-0041 (PIR-011). Adds EQ-ID tagging requirement. Equipment families cannot be finalized until vendor dimensions are confirmed. MRI EQ-020 blocked until OAI-001 resolved. | 42 | Moderate | MULTI_DISCIPLINE_COORDINATION ¦ LONG_LEAD | OFE in Revit with EQ-IDs by 30% DD | shall be modeled | 30% DD milestone |  |  |  | N/A
GR-0096 | HHC-OMR-013 | GR-0085 | Operational & Maintenance Requirements | Design Workflow | Owner RFI Response | Operational | Program Management — Owner Performance | Owner response to design-phase RFIs shall be provided within 10 Business Days of receipt. Heritage PM (Owner's PM) responds to base building and budget RFIs. Tenant Facilities Lead responds to clinical program and operational RFIs. | Owner RFI Response — Design Phase | Design workflow — Owner response standard | Owner RFI response turnaround | 10 Business Days from receipt | All design phases | None | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §6.3 RFI and Clarification Protocol | Inspection | A/E (D. Yuen) — monitor Owner RFI response dates via Procore RFI log | All design phases | Program Management | Owner's Rep — Owner's PM / Tenant Facilities Lead | Owner obligation | Owner response standard complements A/E response standard (GR-0085 — 10 calendar days). Owner uses Business Days; A/E uses calendar days. | GOVERNING | Moderate | Program Management | Owner's obligation — kickoff minutes record | High | SUPPLEMENT to GR-0085 (A/E RFI response 10 calendar days). Establishes Owner-side response obligation. Gallant monitors RFI log — RFIs that add or modify requirements are entered in the register as new events. | 38 | Moderate | MULTI_DISCIPLINE_COORDINATION | 10 Business Days from receipt | within 10 Business Days | all design phases |  |  |  | N/A
GR-0097 | HHC-BCR-005 | GR-0030 | Budget & Cost Requirements | Cost Estimate | Escalation Allowance | Budget | Cost Control — Market Escalation | The 50% SD cost estimate shall carry an explicit escalation allowance reflecting current Albuquerque construction market conditions. Cornerstone Construction (CMAR) has confirmed 6–8% year-over-year escalation for mixed-use work in the Albuquerque market as of Q2 2025. | Construction Cost Escalation Allowance | Cost control — market escalation | Explicit escalation allowance in 50% SD estimate | Albuquerque market: 6-8% year-over-year escalation confirmed by CMAR | 50% SD cost estimate and all subsequent estimates | None | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §4 Budget Review — CMAR Escalation Confirmation | Analysis | Cost Consultant — escalation allowance line item in 50% SD cost estimate | 50% SD gate | Cost Management | Cost Consultant + Cornerstone Construction | CMAR preconstruction scope | SUPPLEMENT to GR-0030 (BCR-004 VE / DD cost reconciliation). Adds explicit escalation allowance requirement at 50% SD. CMAR confirmed 6–8% escalation based on current market conditions. | GOVERNING | High | Cost | CMAR preconstruction scope / Owner cost management | High | SUPPLEMENT to GR-0030. Escalation allowance is now a required line item in all cost estimates. $2.3M current variance means escalation adds further pressure on BCR-001. VE-01 and generator resolution are critical offsets. | 55 | High | HIGH_COST_INFRASTRUCTURE ¦ DECISION_REQUIRED | 6-8% escalation allowance required | shall carry explicit escalation allowance | 50% SD estimate and all subsequent estimates |  |  |  | N/A
GR-0098 | HHC-FR-009 | GR-0003 | Functional Requirements | Physical Therapy | Class IV LASER System | Functional | Clinical — PT Equipment | The physical therapy suite shall accommodate a Class IV Therapeutic LASER System requiring: dedicated 20A/120V GFCI-protected circuit; laser safety zone of minimum 8-foot radius from treatment position; ANSI Z136.1 Class IV laser safety signage at all room entry points and penetrations. Vendor, budget authority, and CF/OFE designation to be confirmed by owner in writing. | PT Class IV LASER System | Clinical service provision — PT equipment | Class IV LASER facility requirements | 20A/120V + 8-ft safety zone + ANSI Z136.1 signage | PT Private Treatment Room 2 | Written owner confirmation required — EQ-CHANGE-001 | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §8.2 EQ-CHANGE-001 / Dr. Nance — Clinical Operations | Inspection | Architect of Record (AOR) / MEP-EOR — verified in 50% SD drawings after written confirmation received | PT Suite, Floor 1 | Architecture / Electrical | Northstar Clinical Operations — Dr. Nance | TI scope — Northstar | Yes | GOVERNING | High | Architecture / Electrical | NNN Lease — TI scope (pending authority confirmation) | Medium | EQ-CHANGE-001. PT LASER: Summus Class IV or LiteCure LightForce. Budget authority ($45K-$85K combined) not confirmed. 50% SD drawings show v1.0 scope only until written direction received. Equipment Schedule Rev. 2 pending. ¦ CLOSED by D11 Directive 3: Class IV LASER (Summus 12W) confirmed and added to program. EQ-CHANGE-001 CLOSED. | 65 | High | DECISION_REQUIRED ¦ HIGH_COST_INFRASTRUCTURE | 20A/120V + 8-ft safety zone + ANSI Z136.1 | N | TBD-UNRESOLVED | written owner confirmation required — EQ-CHANGE-001 | Northstar Clinical Operations — Tenant Facilities Lead / Dr. Nance | June 13, 2025 | Resolved
GR-0099 | HHC-PIR-022 | GR-0003 | Physical & Interface Requirements | Physical Therapy | Traction Table Infrastructure | Physical | Clinical — PT Equipment Infrastructure | If a ceiling-mounted overhead track system is selected for the motorized traction table, structural blocking and load path shall be provided in the PT private treatment rooms at minimum 10 ft above finished floor. Selection between ceiling track and floor-mounted unit requires written owner direction. | PT Motorized Traction Table Infrastructure | Physical infrastructure — PT equipment option | Ceiling track structural blocking if ceiling-mount selected | Structural blocking at 10 ft AFF if ceiling track selected | PT Private Treatment Rooms | Floor-mounted unit requires no structural modification; ceiling track drives structural requirement | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §8.2 EQ-CHANGE-001 / Dr. Nance — Clinical Operations | Inspection | Structural Engineer of Record (SER) — structural blocking shown in 30% DD structural drawings if ceiling track confirmed | PT Private Treatment Rooms, Floor 1 | Structural / Architecture | Northstar Clinical Operations — Dr. Nance | TI scope — Northstar | Yes | GOVERNING | High | Structural / Architecture | NNN Lease — TI scope (pending owner confirmation) | Medium | EQ-CHANGE-001 Part 2. Conditional on ceiling track selection. If floor-mount confirmed, this requirement is inactive. Written direction required per AI-004 by June 13, 2025. ¦ CLOSED by D11 Directive 3: Traction table DEFERRED to Phase 2. Not in current program. A/E should not design ceiling track. | 62 | High | DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | ceiling track structural blocking at 10 ft AFF | N | CONDITIONAL | ceiling track selection TBD — EMBEDDED-CHOICE: ceiling track or floor-mounted | Northstar Clinical Operations — Tenant Facilities Lead / Dr. Nance | June 13, 2025 | Resolved
GR-0100 | HHC-SMR-014 | — | Schedule & Milestone Requirements | Residential Program | Unit Count Decision | Schedule | Structural — Construction Sequencing | The residential unit count (145 units confirmed or 150 units revised) shall be determined by Heritage in writing and transmitted to AOR and Structural Engineer of Record (SER) no later than June 13, 2025. Structural CFS framing design cannot be finalized after 50% SD structural framing plans are issued without structural redesign cost. | Residential Unit Count — Owner Decision | Schedule sequencing — structural design dependency | Unit count decision deadline | Written direction by June 13, 2025 | Before 50% SD structural framing narrative is complete | CFS redesign after July 11 requires fee amendment | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §8.4 PROG-CHANGE-001 / C. Mikkelsen — SER | Inspection | Gallant — written owner direction in project record by June 13, 2025 | Pre-50% SD | Program Management / Structural | Heritage Development Partners — Owner's PM / M. Delgado | Owner scope | Yes | GOVERNING | High | Structural / Cost / Program Management | A/E Contract scope impact | Medium | PROG-CHANGE-001. Developer evaluating 145 → 150 units. CFS framing and load distribution above podium affected. SER: post-SD changes require structural redesign. Decision must precede 50% SD structural framing. ¦ CLOSED by D11 Directive 4: 145-unit residential program confirmed. No change. PROG-CHANGE-001 CLOSED. | 68 | High | DECISION_REQUIRED ¦ HIGH_COST_INFRASTRUCTURE | written direction by June 13, 2025 | N | TBD-UNRESOLVED | 145 vs. 150 units — developer evaluating | Heritage Development Partners — Owner's PM / M. Delgado | June 13, 2025 | Resolved
GR-0101 | HHC-BCR-006 | GR-0027 | Budget & Cost Requirements | Cost Variance | Base Building Overrun | Budget | Cost Control — Variance Watch | The base building construction estimate (Cost Consultant, May 8, 2025) of $44,026,000 exceeds the current baseline by $2,303,000. Combined with the unresolved generator scope (BCR-003), total estimated variance to BCR-001 is approximately $5.8 million. VE-01 (foundation savings pending geotechnical, est. $180K–$340K) and BCR-003 resolution are the primary mitigation paths. No Board amendment authorized; design team directed to design to authorized budget. | Base Building Cost Estimate — Variance | Cost control — estimate variance tracking | Current base building variance vs. baseline | $44,026,000 actual vs. $41,723,000 baseline = $2,303,000 over; combined variance ~$5.8M | 50% SD and all subsequent estimates | VE-01 contingent on geotechnical confirmation; BCR-003 resolution required | MeetingMinutes | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | §4 BCR-UPDATE-001 / Cost Consultant May 8, 2025 | Analysis | Cost Consultant — cost estimate reconciled at 50% SD against BCR-001 | 50% SD cost review | Cost Management | Cost Consultant + Owner's PM (Heritage) | Heritage owner scope | SUPPLEMENT to GR-0027 (BCR-001). Adds current estimate variance data. VE-01 and BCR-003 are the two primary mitigation paths. Cost consultant to attend 50% SD review. Board re-authorization not yet triggered. | GOVERNING | High | Cost / Structural / Electrical | Board Resolution 2024-11 | High | SUPPLEMENT to GR-0027 (BCR-001) and GR-0030 (BCR-004 VE). Establishes the magnitude of variance ($5.8M combined). Design team directed to design to authorized budget. No Board amendment authorized at this time. | 72 | High | HIGH_COST_INFRASTRUCTURE ¦ DECISION_REQUIRED | $5.8M combined variance; design to authorized budget | design to authorized $68M TPC | 50% SD and all subsequent phases |  |  |  | N/A
GR-0102 | HHC-RCR-016 | GR-0021 | Regulatory & Compliance | NM DOH Review | Plan Review Submission | Regulatory | RCR — NM DOH Review Process | NM DOH Office of Facilities Management plan review submission shall occur at 90% CD submittal stage, concurrent with City of Albuquerque building permit application. Package shall include: architectural drawings, HVAC drawings with ASHRAE 170 compliance narrative, electrical drawings with NFPA 99 Category 1 EES documentation, plumbing drawings with medical gas layout, life safety drawings, and NM DOH Form HC-22 FGI 2022 compliance checklist. | NM DOH Plan Review — 90% CD Submission | Regulatory — AHJ plan review sequencing and submission requirements | NM DOH plan review at 90% CD concurrent with City permit | 90% CD submittal; 45–60 calendar day review timeline | AHC occupancy clinical component — Floors 1–2 | NM DOH may issue conditional approval with conditions to be resolved before CoO | Regulatory — AHJ Determination | NM CID/NM DOH AHJ Pre-Application Determination — NM-CID-HFS-2025-0603-HHC · June 3, 2025 | §4 NM DOH Review Process Requirements | Document Review | Owner's Rep / AOR — NM DOH Reference Number confirming complete application | 90% CD gate (est. March 27, 2026) | Architecture / All Engineering | Architect of Record (AOR) | A/E Contract scope | NM DOH plan review is separate AHJ process from City permit. 45–60 day review = critical path to CoO February 1, 2028. | GOVERNING | Critical | Architecture / All Disciplines / Program Management | A/E Contract — code compliance / NM DOH jurisdiction | High | NEW from D9. Critical path: 45–60 day review from March 27, 2026 submission = NM DOH approval by late May/early June 2026, before construction start June 2, 2026. | 88 | Critical | REGULATORY_APPROVAL ¦ SCHEDULE | NM DOH ¦ plan review ¦ 90% CD ¦ CoO | N | N/A |  |  |  | N/A
GR-0103 | HHC-RCR-017 | GR-0102 | Regulatory & Compliance | NM DOH Amendments | NM-001 ICRA | Regulatory | RCR — NM DOH Amendments | An Infection Control Risk Assessment (ICRA) shall be completed and on file with NM DOH prior to permit submission. The ICRA shall be stamped by a licensed infection preventionist per NM DOH Amendment NM-001. | ICRA — NM DOH Pre-Permit Requirement | NM-001 infection control documentation before permit | ICRA stamped by licensed infection preventionist on file with NM DOH before permit submission | Before permit submission | New AHC facility construction in New Mexico | None | Regulatory — State Amendment | NM CID/NM DOH AHJ Pre-Application Determination — NM-CID-HFS-2025-0603-HHC · June 3, 2025 | §5 NM DOH FGI 2022 Amendments — NM-001 | Document Review | NM DOH / Northstar Infection Control Officer | Pre-permit submission gate | Architecture / Infection Control | Northstar Health System | Owner scope — Northstar | ICRA must precede permit. Infection preventionist engagement required during SD/DD. | GOVERNING | High | Regulatory / Clinical Operations | Owner scope — Northstar | High | NEW from D9 NM-001. Infection preventionist not yet engaged — DECISION-PENDING. | 70 | High | REGULATORY_APPROVAL | ICRA ¦ infection control ¦ NM-001 ¦ permit | Y | TBD-UNRESOLVED | Licensed infection preventionist not yet identified | Northstar Health System | 2025-09-01 | Open
GR-0104 | HHC-RCR-018 | GR-0019 | Regulatory & Compliance | NM DOH Amendments | NM-002 RF Shielding | Regulatory | RCR — NM DOH Amendments | RF shielding specifications for the MRI suite shall be reviewed and approved by NM DOH prior to installation. The RF shielding contractor shall be on the New Mexico-licensed specialty contractor list per NM DOH Amendment NM-002. | RF Shielding — NM DOH Pre-Approval | NM-002 RF shielding regulatory approval before installation | NM DOH pre-approval of RF shielding specs; NM-licensed contractor required | Before RF shielding installation | MRI suite RF shielding scope | None — NM-002 has no waiver | Regulatory — State Amendment | NM CID/NM DOH AHJ Pre-Application Determination — NM-CID-HFS-2025-0603-HHC · June 3, 2025 | §5 NM DOH FGI 2022 Amendments — NM-002 | Document Review + Inspection | NM DOH | Before RF shielding installation | Architecture / Electrical | Architect of Record (AOR) / ETS-Lindgren | A/E Contract / RF shielding contractor | NM DOH pre-approval adds lead time to RF shielding procurement — engage ETS-Lindgren by October 31, 2025. | GOVERNING | High | Regulatory / MEP / Procurement | A/E Contract — RF shielding spec | High | NEW from D9 NM-002. Supplements GR-0019 (RF shielding contractor engagement). NM DOH approval is prerequisite to installation. | 72 | High | REGULATORY_APPROVAL ¦ LONG_LEAD | RF shielding ¦ NM-002 ¦ NM DOH ¦ MRI | N | N/A |  |  |  | N/A
GR-0105 | HHC-PIR-016 | GR-0035 | Physical & Interface Requirements | Exam Rooms | NM-004 Minimum Area | Regulatory | PIR — Exam Room Area | All standard patient exam rooms in the AHC clinical floors shall provide a minimum of 120 NSF clear floor area exclusive of toilet rooms and fixed casework per NM DOH Amendment NM-004. Accessible exam rooms shall provide 140 NSF minimum per FGI 2022. | Standard Exam Room — Minimum Clear Area | NM-004 exam room area — stricter than FGI 2022 base standard | Minimum clear floor area per exam room | 120 NSF minimum (standard) · 140 NSF minimum (accessible) | 12 standard exam rooms + 4 accessible exam rooms — Floor 1 | NM-004 overrides FGI 2022 base standard of 100 NSF. No waiver available. | Regulatory — State Amendment | NM CID/NM DOH AHJ Pre-Application Determination — NM-CID-HFS-2025-0603-HHC · June 3, 2025 | §5 NM DOH FGI 2022 Amendments — NM-004 | Design Review + Measurement | NM DOH / Architect of Record (AOR) | All 12 standard exam rooms — Floor 1 | Architecture | Architect of Record (AOR) | A/E Contract — TI design | NM-004 requires 20 NSF increase per standard exam room vs. OPC basis. 12 rooms × 20 NSF = 240 NSF additional program area. Floor plan revision required. | GOVERNING | Critical | Architecture / Program | A/E Contract — clinical TI design | High | NEW REQUIREMENT from D9 NM-004. Design revision required before SD complete. OPC programs standard rooms at 100 NSF — all 12 must be revised to 120 NSF minimum. CONFLICT-PENDING: creates area pressure on clinical floor plan. | 85 | Critical | REGULATORY_APPROVAL ¦ DESIGN_CHANGE | exam room ¦ NM-004 ¦ 120 NSF ¦ floor plan revision | N | N/A |  |  |  | N/A
GR-0106 | HHC-SLR-006 | GR-0035 | Security & Life-Safety | AHC Egress | Travel Distance & Exit Count | Regulatory | SLR — AHC Life Safety | AHC occupancy (Floors 1–2) shall comply with NFPA 101 Chapter 20 egress requirements: maximum 150-foot travel distance to exit from any occupied point; minimum two enclosed exit stairs with stair pressurization per IBC §909; automatic sprinkler protection throughout per NFPA 13 with separate clinical riser. | AHC Egress — Travel Distance / Exit Count / Pressurization | NFPA 101 Chapter 20 AHC egress compliance | Travel distance max / exit count min / pressurization | 150 ft max travel distance · 2 minimum enclosed exit stairs · stair pressurization IBC §909 | AHC occupancy — Floors 1–2 | None — AHC occupancy Chapter 20 requirements are mandatory | Regulatory — AHJ Determination | NM CID/NM DOH AHJ Pre-Application Determination — NM-CID-HFS-2025-0603-HHC · June 3, 2025 | §3 AHC Classification Consequences | Design Review + Inspection | NM CID / Fire Marshal | Clinical Floors 1–2 | Architecture / Mechanical (pressurization) | Architect of Record (AOR) | A/E Contract | Stair pressurization adds mechanical scope. Two enclosed exit stairs required minimum. | GOVERNING | Critical | Architecture / Mechanical / Life Safety | A/E Contract — code compliance | High | NEW from D9 §3. Supplements GR-0035 (corridor width). Stair pressurization per IBC §909 is mechanical scope not previously identified. | 88 | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | AHC ¦ travel distance ¦ exit stair ¦ pressurization ¦ NFPA 101 | N | N/A |  |  |  | N/A
GR-0107 | HHC-PIR-017 | GR-0020 | Physical & Interface Requirements | Foundation System | Shallow Footings VE-01 | Performance | PIR — Foundation | The foundation system shall be designed using shallow spread footings or mat foundation per confirmed Site Class C soil conditions. Allowable bearing capacity: 4,500 psf at minimum 5-foot embedment depth. Minimum footing depth: 36 inches below final grade. | Foundation System — Shallow Footings (VE-01) | Foundation design basis per confirmed geotech — replaces drilled pier assumption | Shallow spread footings or mat foundation; 4,500 psf bearing; 36-inch min depth | 4,500 psf · 36 inches min depth · 5 ft embedment | Site Class C confirmed — ASCE 7-22 | SER to evaluate shallow vs. mat; selection confirmed at 30% DD | Geotechnical Report | Geotechnical Consultant Geotechnical Report SGA-2025-0158 — June 6, 2025 | §3 Foundation Recommendations — VE-01 | Design Review + Special Inspection | Geotechnical Consultant / Structural Engineer of Record (SER) | All foundation elements | Structural | Structural Engineer of Record (SER) | A/E Contract — structural | VE-01 saves $180K–$340K vs. drilled pier basis. Foundation type selection at 30% DD. | GOVERNING | High | Structural / Budget | A/E Contract — structural | High | NEW from D10. VE-01 confirmed. Cost estimate D15 shows $310K savings applied at line 2. | 65 | High | VALUE_ENGINEERING | foundation ¦ shallow footings ¦ VE-01 ¦ Site Class C | N | N/A |  |  |  | N/A
GR-0108 | HHC-PIR-018 | GR-0010 | Physical & Interface Requirements | Seismic Design | Site Class C / SDC C | Regulatory | PIR — Seismic Design | The structural design shall use confirmed ASCE 7-22 Site Class C seismic parameters: Ss = 0.65g, S1 = 0.25g, SDC C. Structural engineer shall recalculate seismic design forces from prior SDC D assumption. | Seismic Design — Confirmed Site Class C / SDC C | Seismic design basis update from SDC D assumption to confirmed SDC C | ASCE 7-22 Site Class C · SDC C · Ss=0.65g · S1=0.25g | Ss = 0.65g · S1 = 0.25g · SDC C | Full building seismic design | SDC C is less restrictive than prior SDC D assumption | Geotechnical Report | Geotechnical Consultant Geotechnical Report SGA-2025-0158 — June 6, 2025 | §3.2 Seismic Design Parameters | Design Review | Structural Engineer of Record (SER) / AHJ | Entire building structural system | Structural | Structural Engineer of Record (SER) | A/E Contract — structural | SDC C allows simplified procedures for some elements. SER to update seismic calculations at 30% DD. | GOVERNING | Moderate | Structural | A/E Contract — structural | High | NEW from D10. SDC C less restrictive than SDC D assumption. No cost increase anticipated. | 55 | Moderate | DESIGN_CHANGE | seismic ¦ SDC C ¦ ASCE 7-22 ¦ Site Class C | N | N/A |  |  |  | N/A
GR-0109 | HHC-PIR-019 | GR-0002 | Physical & Interface Requirements | MRI Suite | Siemens MAGNETOM Altea Design Basis | Physical | PIR — MRI System Design Basis | The MRI suite design shall be based on the confirmed Siemens Healthineers MAGNETOM Altea 1.5T (Product Code XQ26). Design parameters: magnet weight 7,700 lbs; total system weight approx. 25,000 lbs; magnet room clear dimensions 24 ft × 18 ft minimum (432 SF); equipment room 200 NSF minimum; RF shielding per ETS-Lindgren standard specification for MAGNETOM Altea; quench pipe 4-inch diameter to building exterior. | MRI System — Confirmed Siemens MAGNETOM Altea Design Parameters | Lock MRI design basis parameters for structural, MEP, and RF shielding design | Siemens MAGNETOM Altea 1.5T design parameters | 7,700 lb magnet · 25,000 lb total · 432 SF magnet room · 200 NSF equip room · 4-inch quench pipe | MRI suite — Floor 2 | GE SIGNA option eliminated per HHC-ODD-001 Directive 1 | Owner Directive | Heritage Health Campus Owner Written Design Directives HHC-ODD-001 — June 13, 2025 | Directive 1 — MRI Vendor Confirmation | Design Review + Commissioning | Northstar Biomedical / Siemens Healthineers | MRI suite — Floor 2 | Architecture / Structural / Electrical | Architect of Record (AOR) | A/E Contract + OFE (Northstar) | Locks all MRI-dependent design elements. CF-002 and CF-004 resolved. | GOVERNING | Critical | Architecture / Structural / Electrical / RF Shielding | A/E Contract + Northstar OFE | High | NEW from D11 Directive 1. Resolves CF-002 (MRI room area) and CF-004 (MRI point load). Siemens contact: Michael Torres. | 90 | Critical | LONG_LEAD ¦ STRUCTURAL | MRI ¦ Siemens ¦ MAGNETOM Altea ¦ design basis ¦ RF shielding | N | N/A |  |  |  | N/A
GR-0110 | HHC-PIR-020 | — | Physical & Interface Requirements | PT Suite | Class IV LASER Infrastructure | Physical | PIR — PT Equipment Infrastructure | The PT private treatment room 2 shall include infrastructure for a Class IV Therapeutic LASER system (Summus 12W): dedicated 20A/120V GFCI-protected circuit; ANSI Z136.1 Class IV laser safety signage at room entry and all penetrations into the 8-foot laser safety zone; room layout accommodating 8-foot radius laser safety zone. | Class IV LASER — PT Treatment Room Infrastructure | Infrastructure for OFE Class IV LASER confirmed in HHC-ODD-001 | Dedicated 20A/120V GFCI circuit · 8-ft LASER safety zone · ANSI Z136.1 signage | 20A / 120V / GFCI · 8-foot safety zone radius | PT Private Treatment Room 2 — Floor 1 | Traction table ceiling track deferred to Phase 2 — not in current scope | Owner Directive | Heritage Health Campus Owner Written Design Directives HHC-ODD-001 — June 13, 2025 | Directive 3 — PT Equipment | Inspection | Northstar PT Director / AHJ | PT Treatment Room 2 — Floor 1 | Electrical / Architecture | Southwest MEP Engineers | TI scope — clinical electrical | LASER safety zone and dedicated circuit must be shown on SD drawings. | GOVERNING | Moderate | Electrical / Architecture | TI Electrical scope | High | NEW from D11 Directive 3. EQ-CHANGE-001 CLOSED. Cost: $18K TI electrical (D15 line 20). | 45 | Moderate | SAFETY | LASER ¦ Class IV ¦ ANSI Z136.1 ¦ PT ¦ safety zone | N | N/A |  |  |  | N/A
GR-0111 | HHC-BCR-005 | GR-0029 | Budget & Cost Requirements | TI Allowance | Generator Upsize Cost Allocation | Budget | BCR — Cost Allocation | Northstar Health System shall fund the generator upsize cost from 200kW to 350kW (estimated $180,000–$260,000) drawn against the $14,200,000 TI Allowance per NNN Lease Exhibit D. Heritage (Landlord) scope: 200kW base building generator for life safety loads. Northstar (Tenant) scope: incremental cost of upsize to 350kW minimum for NFPA 99 Category 1 EES. | Generator Upsize — Cost Allocation Heritage/Northstar | Document written owner agreement on generator cost allocation | Generator upsize cost $180K–$260K from Northstar TI Allowance | $180,000–$260,000 incremental upsize cost from $14,200,000 TI Allowance | Generator scope — base building + clinical EES | Reduces available TI Allowance for other clinical TI work | Owner Directive | Heritage Health Campus Owner Written Design Directives HHC-ODD-001 — June 13, 2025 | Directive 5 — Generator Scope Allocation | Document Review | Cost Consultant / Owner | Project-wide budget | Program Management | Heritage Development Partners / Northstar Health System | Owner agreement — lease obligation | BCR-003 CLOSED. Generator cost allocation is owner-level decision now recorded. | GOVERNING | High | Budget / Program | NNN Lease Exhibit D | High | NEW from D11 Directive 5. BCR-003 (GR-0029) CLOSED. CF-001 RESOLVED. Actual cost $220K confirmed in D15 cost estimate. | 70 | High | BUDGET | generator ¦ TI allowance ¦ cost allocation ¦ BCR-003 | N | N/A |  |  |  | N/A
GR-0112 | HHC-RCR-019 | — | Regulatory & Compliance | Submittals | Submittal Schedule | Regulatory | RCR — Submittal Requirements | A complete submittal schedule shall be submitted to Owner within 30 days of Notice to Proceed. Submittals required for all Division 11 medical equipment, Division 22 medical gas, Division 23 clinical HVAC systems, and Division 26 EES components. Submittal review period: 14 calendar days. Two review cycles maximum before Owner escalation. | Submittal Schedule and Review Protocol | Establish submittal timeline and review protocol for critical clinical systems | Submittal schedule within 30 days NTP; 14-day review; 2-cycle maximum | 30 calendar days NTP · 14-day review · 2 cycles max | Construction phase | None | Project Specification | Architect of Record (AOR) SD Outline Specifications HHC-SPEC-SD-001 — July 11, 2025 | Div 01 §01 33 00 | Document Review | Owner's Rep / Gallant | Construction phase — all critical clinical systems | Program Management | Cornerstone Construction (CMAR) | CMAR Contract | Submittal schedule is critical path for medical equipment coordination. | GOVERNING | Moderate | Program / Schedule | CMAR Contract | High | NEW from D12 Div 01. Establishes formal submittal protocol. | 50 | Moderate | SCHEDULE | submittals ¦ review period ¦ Division 11 ¦ Division 22 ¦ Division 23 | N | N/A |  |  |  | N/A
GR-0113 | HHC-OMR-038 | — | Operational & Maintenance Requirements | Closeout | O&M Manuals and As-Builts | Operational | OMR — Closeout | O&M manuals, as-built drawings, and equipment warranties shall be delivered to Northstar Health System facilities management no later than 30 calendar days after Substantial Completion, organized by MasterFormat CSI division. Revit as-built model (native file + IFC export) required. All clinical equipment commissioning records shall be included. | Closeout Deliverables — O&M / As-Built / Warranties | Closeout documentation standard for clinical facility handover | O&M manuals + as-built drawings + warranties within 30 days SC; Revit model + IFC export | 30 calendar days after Substantial Completion | Substantial Completion | None | Project Specification | Architect of Record (AOR) SD Outline Specifications HHC-SPEC-SD-001 — July 11, 2025 | Div 01 §01 78 00 | Document Review | Northstar Facilities Management / Owner's Rep | All systems — entire building | Program Management | Cornerstone Construction (CMAR) | CMAR Contract | Revit as-built model required — sets BIM standard for A/E and CMAR. | GOVERNING | Moderate | Program / Operations | CMAR Contract | High | NEW from D12 Div 01 §01 78 00. IFC export adds interoperability requirement for Northstar FM systems. | 48 | Moderate | SCHEDULE | O&M ¦ as-built ¦ Revit ¦ IFC ¦ closeout ¦ warranties | N | N/A |  |  |  | N/A
GR-0114 | HHC-RCR-020 | GR-0102 | Regulatory & Compliance | BIM Coordination | Clash Detection Protocol | Regulatory | RCR — BIM Coordination | The A/E team shall maintain a federated BIM model in Autodesk Revit. Clash detection reports using Navisworks are required at 50% SD, 60% DD, and 90% CD. The A/E shall maintain a coordination log and transmit to Owner's Representative within 3 business days of each clash detection run. | BIM Coordination — Clash Detection Protocol | Mandatory clash detection schedule for complex mixed-use building | Federated Revit model; Navisworks clash detection at 50% SD, 60% DD, 90% CD; 3-day transmittal | 3 business days transmittal after each clash detection run | Design phase — 50% SD through 90% CD | None | Project Specification | Architect of Record (AOR) SD Outline Specifications HHC-SPEC-SD-001 — July 11, 2025 | Div 01 §01 31 00 | Document Review | Owner's Rep / Gallant | All design disciplines | Architecture / All Engineering | Architect of Record (AOR) | A/E Contract | BIM coordination is active — 50% SD clash run already produced BIM Issues Log (D13). | GOVERNING | Moderate | Architecture / All Engineering / Program | A/E Contract | High | NEW from D12 Div 01 §01 31 00. 50% SD clash run completed — D13 BIM Issues Log is the output. | 52 | Moderate | COORDINATION | BIM ¦ clash detection ¦ Revit ¦ Navisworks ¦ coordination | N | N/A |  |  |  | N/A
GR-0115 | HHC-PIR-021 | GR-0002 | Physical & Interface Requirements | MRI Suite | Zone IV RF Duct Penetration | Physical | PIR — MRI Zone Compliance | All supply air ducts entering the MRI Zone IV envelope shall be provided with RF-shielded duct penetrations or rerouted outside the Zone IV boundary. No unshielded duct penetrations are permitted in the ACR-defined Zone IV boundary. | MRI Zone IV — RF-Shielded Duct Penetrations | ACR Zone IV boundary integrity — prevent RF leakage via ductwork | RF-shielded penetrations or reroute outside Zone IV | Zero unshielded duct penetrations in Zone IV | All ductwork at or near MRI Zone IV envelope | Coordinate with RF shielding contractor (ETS-Lindgren) | BIM Coordination | Architect of Record (AOR) 50% SD BIM Coordination Issues Log Rev 0.5 — July 11, 2025 | BIM-001 — CRITICAL | Design Review + RF Testing | ACR / RF Shielding Contractor | MRI Zone IV boundary — Floor 2 | Mechanical / Architecture | Southwest MEP Engineers | A/E Contract — TI MEP | BIM-001 clash found duct penetrating Zone IV at Grid C-4. MEP-EOR + AOR to resolve at 30% DD. | CONFLICT-PENDING | Critical | MEP / Architecture / RF Shielding | A/E Contract — TI MEP + RF shielding | High | NEW from D13 BIM-001 CRITICAL clash. CF-008 flagged. Resolution: reroute duct OR provide RF-shielded penetration. | 88 | Critical | DESIGN_CONFLICT ¦ REGULATORY_APPROVAL | MRI ¦ Zone IV ¦ RF ¦ duct penetration ¦ ACR ¦ BIM-001 | N | N/A |  |  |  | N/A
GR-0116 | HHC-PIR-022 | GR-0003 | Physical & Interface Requirements | PT Suite | Open Gym Column-Free Span | Physical | PIR — PT Structural | The PT open gym area shall be column-free for the full 800 SF minimum program area. The structural system shall provide a long-span solution eliminating the column at Grid E-5 currently shown in the structural model. | PT Open Gym — Column-Free Structural Span | Enforce column-free PT gym requirement against structural model conflict | Column-free PT open gym — 800 SF minimum | 800 SF column-free minimum | PT open gym — Floor 2 | SER to evaluate long-span alternative at Grid E-5 at 30% DD | BIM Coordination | Architect of Record (AOR) 50% SD BIM Coordination Issues Log Rev 0.5 — July 11, 2025 | BIM-010 — MEDIUM | Design Review | Structural Engineer of Record (SER) / Northstar PT Director | PT open gym — Floor 2 | Structural / Architecture | Structural Engineer of Record (SER) | A/E Contract — structural | BIM-010: column at Grid E-5 violates PT gym column-free requirement. Long-span joist or PT transfer beam required. | CONFLICT-PENDING | High | Structural / Architecture | A/E Contract — structural | High | NEW from D13 BIM-010. SER to resolve at 30% DD. CF-007 flagged. | 68 | High | STRUCTURAL ¦ DESIGN_CONFLICT | PT gym ¦ column-free ¦ BIM-010 ¦ long-span ¦ structural | N | N/A |  |  |  | N/A
GR-0117 | HHC-PIR-023 | — | Physical & Interface Requirements | PT Slab | Level 3 Floating Floor FTC | Physical | PIR — Level 3 Floor Height | The Level 3 residential floor design shall account for the acoustic floating floor system required by NM DOH Amendment NM-003 (STC 60/IIC 55). The floating floor adds approximately 3–4 inches to finished floor height at Level 3. Level 3 floor-to-ceiling clearance design shall incorporate this addition. | Level 3 Floor-to-Ceiling Clearance — Floating Floor Addition | Coordinate acoustic overlay height with Level 3 residential FTC design | 3–4 inch floating floor addition to Level 3 FTC | 3–4 inches additional FH at Level 3 | Level 3 residential — entire floor | Cost: $195,000 (D15 line 13) | BIM Coordination | Architect of Record (AOR) 50% SD BIM Coordination Issues Log Rev 0.5 — July 11, 2025 | BIM-002 / CMAR Review §2.2 | Design Review | Architect of Record (AOR) | Level 3 residential — entire floor | Architecture / Structural | Architect of Record (AOR) | Base building scope | NM-003 floating floor is mandatory (no waiver). Level 3 FTC must absorb 3–4 inch addition. | GOVERNING | High | Architecture / Structural / Acoustic | A/E Contract — base building | High | NEW from D13 BIM-002 / D14 CMAR §2.2. Acoustic subconsultant to coordinate with A/E at DD. | 65 | High | REGULATORY_APPROVAL ¦ DESIGN_CHANGE | floating floor ¦ Level 3 ¦ FTC ¦ NM-003 ¦ acoustic | N | N/A |  |  |  | N/A
GR-0118 | HHC-PIR-024 | GR-0015 | Physical & Interface Requirements | EES | EES Circuit Physical Separation | Regulatory | PIR — NFPA 99 EES | All NFPA 99 Category 1 EES circuits shall be routed in physically separate conduit from normal power circuits. Red color coding is required on all EES conduit. Three EES circuits currently shown in normal power conduit at Grid B-2 to D-4 (clinical corridor) shall be rerouted. | EES Circuit — Physical Separation from Normal Power | NFPA 99 Chapter 6 EES physical separation compliance | EES circuits in separate conduit from normal power; red color coding | Zero EES circuits in normal power conduit | Clinical corridor EES circuits — Floors 1–2 | None — NFPA 99 Chapter 6 is mandatory | BIM Coordination | Architect of Record (AOR) 50% SD BIM Coordination Issues Log Rev 0.5 — July 11, 2025 | BIM-009 — MEDIUM | Inspection | AHJ / Cx Agent | All EES circuits — clinical floors | Electrical | Southwest MEP Engineers | A/E Contract — TI electrical | BIM-009 clash: 3 EES circuits in normal power conduit — code violation must be corrected before CD. | CONFLICT-PENDING | High | Electrical / Life Safety | A/E Contract — TI electrical | High | NEW from D13 BIM-009. MEP-EOR to correct conduit routing. Red color coding required. | 72 | High | LIFE_SAFETY ¦ REGULATORY_APPROVAL | EES ¦ NFPA 99 ¦ conduit separation ¦ BIM-009 ¦ red conduit | N | N/A |  |  |  | N/A
GR-0119 | HHC-PIR-025 | GR-0109 | Physical & Interface Requirements | MRI Suite | MRI Delivery Opening | Physical | PIR — MRI Construction Sequencing | Construction documents shall include a temporary MRI delivery opening in the east wall of the imaging suite (minimum 10 ft × 10 ft) that is formed-but-not-closed during the structural slab pour at Level 2. A temporary partition detail shall permit weather protection while remaining removable for MRI delivery. The construction schedule shall include a milestone: "MRI delivery window open" at least 4 weeks before "MRI magnet room wall enclosure." | MRI Delivery Opening — Construction Sequencing Requirement | Ensure MRI magnet can be delivered and set before imaging suite wall enclosure | 10 ft × 10 ft minimum delivery opening; 4-week minimum before wall enclosure | 10 ft × 10 ft minimum · 4 weeks minimum lead before enclosure | MRI magnet delivery — construction phase | Not addressed in any prior source document — new CMAR-identified requirement | Constructability Review | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 — July 18, 2025 | §2.1 MRI Delivery Window — CRITICAL PATH | Schedule Review + Field Inspection | CMAR / GC Superintendent | MRI magnet room — Floor 2 | Architecture / Structural | Cornerstone Construction (CMAR) | CMAR Construction scope | If MRI is not set before wall enclosure, demolition required — catastrophic schedule and cost impact. | GOVERNING | Critical | Architecture / Structural / Schedule | CMAR Contract + A/E Contract | High | NEW from D14 CMAR §2.1. Source: Constructability Review only. Not in any design document. Must be added to CDs. | 92 | Critical | LONG_LEAD ¦ SCHEDULE ¦ STRUCTURAL | MRI delivery ¦ wall enclosure ¦ construction sequence ¦ CMAR ¦ critical path | N | N/A |  |  |  | N/A
GR-0120 | HHC-SMR-009 | — | Schedule & Milestone Requirements | Utilities | Gas Service Permit Timeline | Schedule | SMR — Utility Procurement | The gas service permit application to NM Gas Company shall be submitted concurrently with the building permit, not after. NM Gas Company requires a minimum 12-week lead from permit application to service installation for commercial high-pressure gas service. The gas service route from Lomas Blvd main to the generator pad shall be confirmed in the SD site plan before permit submission. | Gas Service Permit — Concurrent with Building Permit | Prevent gas service delay from causing generator start delay | Gas permit concurrent with building permit; 12-week NM Gas Company lead | 12-week minimum lead from permit to service installation | Generator natural gas service | Generator pad location must be confirmed in SD before permit | Constructability Review | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 — July 18, 2025 | §2.3 Generator Pad / Gas Service | Schedule Review | CMAR / Owner | Generator pad — site plan | Electrical / Civil | Cornerstone Construction (CMAR) | CMAR Contract + A/E Contract | Generator pad location TBD — DECISION-PENDING. Gas route cannot be designed until pad is confirmed. | GOVERNING | High | MEP / Schedule / Civil | CMAR Contract + A/E Contract | High | NEW from D14 CMAR §2.3. Generator pad location is DECISION-PENDING (GR-0121). 12-week lead is critical path for generator commissioning. | 72 | High | SCHEDULE ¦ LONG_LEAD | gas service ¦ NM Gas Company ¦ permit ¦ generator ¦ 12-week lead | N | N/A |  |  |  | N/A
GR-0121 | HHC-PIR-026 | GR-0120 | Physical & Interface Requirements | Site | Generator Pad Location | Physical | PIR — Site / Generator | Generator pad location shall be confirmed in SD site plan drawings before permit submission. Generator exhaust routing requires 20-foot minimum clearance from building openings. Site constraints on the 1.4-acre site require early coordination of generator pad location with exhaust routing design. | Generator Pad Location — SD Confirmation Required | Confirm generator pad location to enable gas route and exhaust design | Generator pad location confirmed in SD; 20-ft exhaust clearance from openings | 20-foot minimum exhaust clearance from building openings | SD site plan | Site is 1.4 acres — exhaust clearance is constrained | Constructability Review | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 — July 18, 2025 | §2.3 Generator Pad Location | Design Review | Architect of Record (AOR) / Southwest MEP | Site plan — 1500 Lomas Blvd NE | Architecture / Electrical / Civil | Architect of Record (AOR) | A/E Contract | Generator pad location drives gas route, exhaust routing, and gas permit timeline. | DECISION-PENDING | High | Architecture / MEP / Civil | A/E Contract | High | NEW from D14 CMAR §2.3. Generator pad location TBD on 50% SD — must be resolved before SD complete. | 68 | High | DECISION_REQUIRED ¦ SCHEDULE | generator pad ¦ site plan ¦ exhaust ¦ 20-foot clearance | Y | TBD-UNRESOLVED | Generator pad location shown TBD on 50% SD site plan | Architect of Record (AOR) / Southwest MEP | 2025-08-15 | Open
GR-0122 | HHC-SMR-010 | GR-0023 | Schedule & Milestone Requirements | Elevator | Contractor Engagement — SD Phase | Schedule | SMR — Elevator Procurement | Elevator contractor engagement shall begin during SD phase. The 52–64 week lead time for 4-cab, 7-stop commercial elevator systems requires immediate procurement initiation. Elevator shaft dimensions and pit dimensions shall be confirmed in SD drawings before elevator contract execution. | Elevator Contractor Engagement — SD Phase Requirement | Critical-path elevator procurement not previously identified | Elevator contractor engagement during SD phase; shaft dimensions confirmed in SD | 52–64 week lead time; 4 cabs, 7 stops | Base building scope | Shaft dimensions must precede contract | Constructability Review | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 — July 18, 2025 | §3 Long-Lead Procurement — Elevator | Schedule Review | CMAR / Owner | Base building — elevator shafts | Architecture / Structural | Cornerstone Construction (CMAR) | CMAR Contract | Not in any prior document. 52–64 week lead is critical path for Oct 2026 shaft-ready milestone. | DECISION-PENDING | Critical | Architecture / Structural / Schedule | CMAR Contract | High | NEW from D14 CMAR §3. Elevator lead time critical path. Shaft dimensions DECISION-PENDING. D15 shows $1.92M elevator budget. | 82 | Critical | LONG_LEAD ¦ DECISION_REQUIRED ¦ SCHEDULE | elevator ¦ long-lead ¦ shaft ¦ CMAR ¦ 52-64 weeks | Y | TBD-UNRESOLVED | Elevator shaft dimensions not confirmed in 50% SD drawings | Architect of Record (AOR) + Structural Engineer of Record (SER) | 2025-09-01 | Open
GR-0123 | HHC-BCR-006 | GR-0025 | Budget & Cost Requirements | SD Estimate | Base Building Budget | Budget | BCR — Cost Tracking | Total project cost at 50% SD shall be tracked against the $68M TPC ceiling. Current 50% SD estimate: Base Building $30,927,000 (under baseline by $1,693,000 due to VE-01 foundation savings); Residential $23,295,000 (over baseline by $595,000 due to NM-003 acoustic overlay); Retail $985,000; Clinical TI $12,180,000. Total SD estimate: $67,387,000 — within $68M TPC ceiling with $613,000 contingency. | SD Cost Estimate — TPC Reconciliation | Track total project cost against $68M ceiling at 50% SD gate | $68M TPC ceiling; SD estimate $67.387M; contingency $613K | $67,387,000 SD estimate · $613,000 remaining contingency | 50% SD milestone | Residential over baseline by $595K (acoustic overlay NM-003 $195K + escalation $340K + other $60K) | Cost Estimate | Cost Consultant 50% SD Cost Estimate — July 18, 2025 | SD Cost Estimate — Summary | Cost Review | Cost Consultant / Owner | Project-wide | Program Management | Heritage Development Partners | Owner scope | $613K contingency is thin. Any scope additions must be evaluated against TPC ceiling. | GOVERNING | Critical | Program / Budget | Owner Contract | High | NEW from D15. SD estimate within TPC ceiling but contingency thin. NM-003 acoustic overlay ($195K) and generator upsize ($220K) are new costs since baseline. | 85 | Critical | BUDGET | TPC ¦ SD estimate ¦ cost reconciliation ¦ $68M ¦ contingency | N | N/A |  |  |  | N/A
GR-0124 | HHC-BCR-007 | GR-0026 | Budget & Cost Requirements | TI Allowance | SD TI Estimate | Budget | BCR — TI Cost Tracking | Clinical TI Allowance utilization at 50% SD: Base TI construction $9,380,000; Medical equipment installation $695,000; Clinical MEP $1,890,000; Clinical electrical $1,270,000; Generator upsize (BCR-003) $220,000; Class IV LASER infrastructure $18,000. Total TI estimate: $13,473,000. Remaining TI allowance vs. $14,200,000 ceiling: $727,000. | TI Allowance — SD Cost Utilization Tracking | Track TI Allowance utilization against $14.2M ceiling at 50% SD | $14.2M TI ceiling; SD TI estimate $13.473M; remaining $727K | $13,473,000 TI estimate · $727,000 remaining TI allowance | 50% SD milestone | Generator upsize ($220K) and LASER ($18K) are new items drawing against TI | Cost Estimate | Cost Consultant 50% SD Cost Estimate — July 18, 2025 | Clinical TI Cost Summary | Cost Review | Cost Consultant / Northstar | Clinical TI scope | Program Management | Northstar Health System | Lease obligation — Northstar | $727K remaining TI allowance. Any new TI scope items require TI ceiling impact assessment. | GOVERNING | Critical | Program / Budget | NNN Lease Exhibit D | High | NEW from D15. TI within ceiling but $727K remaining is thin given design is only at 50% SD. DD escalation is a risk. | 82 | Critical | BUDGET | TI allowance ¦ $14.2M ¦ clinical TI ¦ SD estimate ¦ cost tracking | N | N/A |  |  |  | N/A

## Decision_Register
HERITAGE HEALTH CAMPUS · DECISION REGISTER · DECISION-PENDING ITEMS · v2.0 · © 2026 GALLANT PROJECT SOLUTIONS LLC
Req ID | Requirement Statement (Summary) | Decision Type | Trigger Language | Required Action | Decision Owner | Deadline | Status
GR-0002 |  | TBD-UNRESOLVED | model TBD — MRI vendor under active |  | Northstar Biomedical Engineeri | June 13, 2025 | Resolved — see register notes
GR-0018 |  | TBD-UNRESOLVED | model TBD — vendor under active eva |  | Northstar Biomedical Engineeri | June 13, 2025 | Resolved — see register notes
GR-0019 |  | TBD-UNRESOLVED | not yet completed |  | Northstar — Infection Preventi | June 27, 2025 | Open
GR-0020 |  | TBD-UNRESOLVED | not yet received |  | Heritage Development Partner | OVERDUE — June 6, | Resolved — see register notes
GR-0021 |  | CONDITIONAL | FGI edition confirmation pending |  | Architect of Record (AOR) — | May 23, 2025 | Resolved — see register notes
GR-0022 |  | CONDITIONAL | Procurement shall not begin before |  | Owner's PM (Heritage) + K. Oka | October 31, 2025 | Open
GR-0023 |  | CONDITIONAL | shall not precede MRI model confirm |  | Northstar / GC Preconstruction | October 31, 2025 ( | Open
GR-0029 |  | EMBEDDED-CHOICE | shall be assigned in writing — cost |  | Owner's PM (Heritage) + K. Oka | July 11, 2025 | Resolved — see register notes
GR-0033 |  | TBD-UNRESOLVED | 200 NSF (Siemens) vs. 240 NSF (GE) |  | Northstar Biomedical Engineeri | June 13, 2025 (per | Resolved — see register notes
GR-0035 |  | CONDITIONAL | conditional on AHC occupancy confir |  | AOR + NM DOH (AHJ | Per SMR-005 — May | Resolved — see register notes
GR-0036 |  | EMBEDDED-CHOICE | Exhibit D is silent — procurement b |  | Owner's PM (Heritage) + K. Oka | July 11, 2025 | Resolved — see register notes
GR-0038 |  | TBD-UNRESOLVED | additional locations per OAI-004 |  | Northstar Clinical Director | Prior to 50% SD | Open
GR-0039 |  | TBD-UNRESOLVED | 25,000 lb point load — vendor-speci |  | Northstar Biomedical Engineeri | June 13, 2025 | Resolved — see register notes
GR-0043 |  | CONDITIONAL | FGI 2022 planning basis — AHJ confi |  | Architect of Record (AOR) ( | May 23, 2025 | Resolved — see register notes
GR-0044 |  | CONDITIONAL | AHC classification assumed — pendin |  | Architect of Record (AOR) ( | Per SMR-005 | Resolved — see register notes
GR-0051 |  | CONDITIONAL | placement governed by ICRA — not ye |  | Northstar Infection Prevention | June 27, 2025 (per | Open
GR-0056 |  | CONDITIONAL | conditional on BCR-003 generator re |  | Owner's PM + Tenant Facilities Lead (per BC | July 11, 2025 | Open
GR-0098 |  | TBD-UNRESOLVED | written owner confirmation required |  | Northstar Clinical Operations | June 13, 2025 | Resolved — see register notes
GR-0099 |  | CONDITIONAL | ceiling track selection TBD — EMBED |  | Northstar Clinical Operations | June 13, 2025 | Resolved — see register notes
GR-0100 |  | TBD-UNRESOLVED | 145 vs. 150 units — developer evalu |  | Heritage Development Partner | June 13, 2025 | Resolved — see register notes
GR-0103 |  | TBD-UNRESOLVED | Licensed infection preventionist not yet identified |  | Northstar Health System | 2025-09-01 | Resolved — see register notes
GR-0121 |  | TBD-UNRESOLVED | Generator pad location shown TBD on 50% SD site plan |  | Architect of Record (AOR) / Southwest MEP | 2025-08-15 | Overdue
GR-0122 |  | TBD-UNRESOLVED | Elevator shaft dimensions not confirmed in 50% SD drawings |  | Architect of Record (AOR) + Structural Engineer of Record (SER) | 2025-09-01 | Overdue

## Conflict_Register
HERITAGE HEALTH CAMPUS · CONFLICT DETECTION REGISTER · v2.0 · © 2026 GALLANT PROJECT SOLUTIONS LLC
Conflict ID | Conflict Type | Req ID A | Req ID B | Conflict Description | Value / Obligation A | Value / Obligation B | Recommended Action | Status
CF-001 | ParameterConflict |  |  | Generator capacity: OPC estimates 150kW minimum for clinical EES; Programming Doc base building generator 200kW for life safety. Combined NFPA 99 Category 1 requirement = 350kW minimum. Neither document acknowledges the combined load requirement or assigns the cost delta. | OPC §4.2: '150 kW minimum for clinical TI loads — confirm with electrical engineer during SD' | Programming Doc §C: 'Base building generator 200kW life safety loads' — separate from clinical EES | Heritage PM and Northstar Facilities to align on 350kW combined minimum. Assign cost responsibility for 200kW→350kW upsize ($180K–$260K est.) in written project memo before 50% SD gate. CMAR to include generator in construction schedule with 20–28 week lead. | RESOLVED
CF-002 | ParameterConflict |  |  | MRI equipment room area: OPC programs 200 NSF for equipment room. Equipment Schedule lists both Siemens MAGNETOM Altea (200 NSF equipment room) and GE SIGNA Creator (240 NSF equipment room) as under active evaluation. Two contradictory equipment room sizes in the same source document. | OPC §B Imaging Suite: MRI Equipment Room 200 NSF | Equipment Schedule EQ-021 Note: 'GE SIGNA requires ~240 NSF equipment room vs. 200 NSF current program' | MRI vendor selection (OAI-001, GR-0018) resolves this conflict. Design team proceeds on Siemens 200 NSF basis. If GE is selected, imaging suite floor plan requires revision — 40 NSF reallocation. A/E to flag in 50% SD area compliance summary. | RESOLVED
CF-003 | ScopeConflict |  |  | Clinical AHU scope boundary: OPC requires dedicated clinical AHUs separate from base building residential and retail HVAC systems. Programming Document references NNN Lease Exhibit D (Landlord Work / Tenant Work Matrix) which is silent on AHU procurement. Neither base building nor TI scope is explicitly assigned. | OPC §4.1: 'Northstar requires dedicated HVAC systems serving the clinical component, separate from the base building residential and retail systems' | Programming Doc §C / NNN Lease Exhibit D: Exhibit D is silent on clinical AHU procurement — not listed as Landlord Work or Tenant Work | Heritage PM and Northstar Facilities to resolve AHU scope boundary in writing (project memo or lease side letter) before 50% SD gate. CMAR cannot begin AHU procurement (12–18 week lead) without scope assignment. A/E to identify AHU locations in 50% SD HVAC narrative. | OPEN
CF-004 | ParameterConflict |  |  | MRI structural design basis: Equipment Schedule lists both Siemens MAGNETOM Altea (magnet weight 7,700 lbs) and GE SIGNA Creator (magnet weight ~8,100 lbs) as under active evaluation. Structural engineer cannot design to two different point loads simultaneously. 400 lb difference is structurally significant in PT flat plate design. | Equipment Schedule EQ-020: 'Siemens MAGNETOM Altea — magnet weight 7,700 lbs' | Equipment Schedule EQ-020 Note: 'GE SIGNA also under evaluation — est. magnet weight ~8,100 lbs' | Structural engineer proceeding on Siemens 7,700 lb basis per kickoff meeting agreement. If GE is selected, structural MRI room slab and foundation design must be revised. Vendor decision required by June 13, 2025 (GR-0018 / SMR-002) before 30% DD structural narrative is finalized. | RESOLVED
CF-005 | AuthorityConflict |  |  | Governing FGI edition: TJC Regulatory Requirements Summary requires compliance with FGI 2022 Outpatient Guidelines. TJC standard requires compliance with the 'latest adopted edition' per AHJ. No document in the 5-source set confirms that NM DOH has adopted FGI 2022. Pre-application research indicates NM DOH may be on FGI 2018. | TJC Summary RQ-002: 'For all new construction, the organization shall comply with the latest adopted edition of the FGI Guidelines per the AHJ jurisdiction' | TJC Summary / AHJ confirmation: NM DOH adoption of FGI 2022 not confirmed in any source document. AHJ may require FGI 2018. | A/E to submit pre-application to NM DOH by May 23, 2025 (GR-0021 / SMR-005) confirming: (1) applicable FGI edition; (2) NM-specific amendments; (3) AHC occupancy classification. Design proceeds on FGI 2022 basis. If FGI 2018 confirmed, A/E to identify all affected requirements and issue design directive. | RESOLVED
CF-006 | ScopeConflict |  |  | STC 60 assembly cost and scope: TJC document requires STC 60 / IIC 55 between Level 2 clinical and Level 3 residential. This performance cannot be achieved by the 8-inch post-tensioned flat plate structural system alone. Acoustic overlay or floating floor system on the residential side is required. Neither the OPC nor the Programming Document allocates the cost or assigns scope responsibility for this acoustic upgrade. | TJC Summary RQ-019: 'Minimum STC 60 between clinical floors (Levels 1–2) and residential floors (Level 3 and above). Floor/ceiling assembly between Level 2 clinic and Level 3 residential must achieve STC 60 / IIC 55.' | Programming Doc §C / OPC: Neither document budgets for acoustic overlay ($80K–$150K est.) or assigns scope responsibility (base building vs. residential TI) | Acoustic subconsultant to confirm minimum assembly meeting STC 60 at 30% DD analysis. A/E to identify cost allocation of acoustic overlay to Owner (Heritage or Northstar) before 60% DD. Cost to be incorporated in BCR-004 VE review at DD gate. | OPEN
CF-007 | ScopeConflict |  |  | PT open gym column-free requirement vs. structural model: PIR requirement mandates 800 SF column-free PT open gym. BIM clash BIM-010 shows a 14-inch concrete column at Grid E-5 within the required column-free zone. Program requirement and structural model are irreconcilable without design revision. | GR-0003: '800 SF column-free open gym' per Owner Program Criteria | GR-0116 / BIM-010: '14-inch round concrete column at Grid E-5 within PT open gym' | Structural Engineer of Record (SER) to evaluate long-span alternative at Grid E-5 at 30% DD (post-tensioned transfer beam or long-span joist). Structural revision required before 60% DD. | OPEN
CF-008 | ParameterConflict |  |  | MRI Zone IV duct penetration and EES conduit routing: Two separate NFPA/ACR compliance failures identified in BIM coordination run. (1) Supply air duct penetrates ACR Zone IV boundary without RF-shielded penetration at Grid C-4. (2) Three EES circuits routed in normal power conduit per NFPA 99 §6 violation at Grid B-2 to D-4. | GR-0115: ACR Zone IV requires zero unshielded duct penetrations in Zone IV boundary | GR-0118: NFPA 99 Ch. 6 requires EES circuits physically separated from normal power | MEP-EOR: (1) reroute supply duct outside Zone IV OR provide RF-shielded penetration at Grid C-4; (2) reroute 3 EES circuits to separate conduit with red color coding. Both items resolve before 60% DD. | OPEN

## Lineage_Log
HERITAGE HEALTH CAMPUS · DOCUMENT LINEAGE LOG — CHAIN OF CUSTODY · v2.0 · © 2026 GALLANT PROJECT SOLUTIONS LLC
Entry# | Document Name | Document Type | Version / Revision | Document Issue Date | Processing Date | Processing Mode | Register Version After | Requirements Added | Requirements Modified | Relationship Summary | Authority Level | Notes
1 | Northstar TJC Regulatory Requirements Summary v1.0 | Regulatory Requirements Summary | v1.0 | 2025-01-15 | 2025-01-28 | Single-pass | v1.0 | 22 |  | 22 NEW, 0 SUPPLEMENT, 0 CONFLICT, 0 MATCH | Standard/Code — Governing — Prescriptive — High | 26 TJC requirements processed. 22 extracted as distinct register records; 4 consolidated into parent requirements. RCR and SLR categories seeded.
2 | Heritage Health Campus Owner Program Criteria Rev. 2 | Owner Program Requirements | Rev. 2 | 2024-12-10 | 2025-01-28 | Single-pass | v1.0 | 24 |  | 24 NEW, 0 SUPPLEMENT, 0 CONFLICT, 0 MATCH | OwnerCriteria — Owner-Directive — Prescriptive — High | FR, PIR, PR, and OMR categories seeded. OPC is the primary program document; TJC requirements remain governing for regulatory matters.
3 | Heritage Health Campus Programming Document v1.0 | Owner Budget Authorization | v1.0 | 2024-12-01 | 2025-01-28 | Single-pass | v1.0 | 8 |  | 8 NEW (BCR + SMR budget), 0 SUPPLEMENT, 1 CONFLICT detected, 0 MATCH | OwnerBudgetAuth — Owner-Directive — Interpretive — Standard | BCR-001, BCR-002, BCR-003, BCR-004 and 4 SMR budget/schedule requirements extracted. CF-001 (generator capacity) detected in cross-document comparison with D2. CF-003 (AHU scope) detected in cross-document comparison with D2.
4 | Heritage Health Campus Milestone Schedule v1.0 | Program Schedule Document | v1.0 | 2024-12-01 | 2025-01-28 | Single-pass | v1.0 | 6 |  | 6 NEW (SMR schedule milestones), 4 SUPPLEMENT, 0 CONFLICT, 0 MATCH | ProgramDoc — Owner-Directive — Interpretive — Standard | SMR requirements extracted and linked to Programming Document parent requirements. Milestone schedule adds sequencing specificity not in Programming Document narrative.
5 | Northstar Clinic Equipment Schedule v1.0 | OFE Document | v1.0 | 2025-01-22 | 2025-01-28 | Single-pass | v1.0 | 10 |  | 10 NEW (PIR + OMR equipment interface), 0 SUPPLEMENT, 2 CONFLICT detected, 0 MATCH | OFEDoc — Owner-Directive — Interpretive — High | CF-002 (MRI equipment room area) and CF-004 (MRI structural point load — two vendor options) detected. Equipment facility inputs seed PIR requirements not present in OPC.
6 | Albuquerque/NM Commercial Building Code (14.7.2 NMAC — 2021 NMCBC) | AHJ-Adopted Code | Effective July 19, 2023 | 2023-07-19 | 2025-01-28 | Single-pass | v1.1 | 10 |  | 10 NEW (RCR + PIR + SER + SLR), 7 SUPPLEMENT (to baseline requirements), 0 CONFLICT detected, 0 MATCH | Code — AHJ-Adopted — Governing — Prescriptive — High | ABQ/NM Commercial Building Code (14.7.2 NMAC). Confirms NMCBC (IBC 2021 + NM amendments) as governing commercial code. Adds NM-specific requirements: baby changing facilities (NMSA 50-13-10.5), NMMC/NMPC trade code substitutions, stairway dimensions, Type IA construction confirmation, NMCECC energy code. Supplements 7 existing baseline requirements. Partially informs DF-NEW-001 (confirms commercial base code; FGI remains NM DOH jurisdiction).
7 | Heritage Health Campus A/E Request for Proposals v1.0 — HHC-2025-AE-001 | Request for Proposals | v1.0 | 2025-04-15 | 2025-05-01 | Single-pass | v1.2 | 13 | 93 | 13 NEW: SMR/PIR/BCR/SLR procurement and scope requirements · 9 MATCH · 4 SUPPLEMENT | OwnerDirective — Prescriptive — Standard | A/E RFP establishes scope boundary, submission requirements, and long-lead procurement alerts.
8 | Heritage Health Campus A/E Design Services Kickoff Meeting Minutes — May 12, 2025 | Meeting Minutes | Official Record | 2025-05-14 | 2025-05-14 | Single-pass | v1.3 | 8 | 101 | 8 NEW: SMR/PIR/BCR/FR program changes · 9 MATCH · 3 SUPPLEMENT · 3 STATUS UPDATES | MeetingMinutes — Owner-Directive — Interpretive — Standard | Official project record per unobjected minutes rule. Three new DECISION-PENDING (GR-0098 PT LASER, GR-0099 traction table, GR-0100 unit count). BCR-UPDATE-001 $2.3M overrun surfaced.
9 | NM CID/NM DOH AHJ Pre-Application Determination — NM-CID-HFS-2025-0603-HHC · June 3, 2025 | AHJ Determination Letter | Official | 2025-06-03 | 2025-06-03 | Single-pass | v1.4 | 5 | 106 | 5 NEW (RCR/PIR/SLR from AHJ determinations + NM amendments) · Status updates: GR-0043, GR-0021, GR-0035, GR-0044 → GOVERNING · CF-005 RESOLVED | RegulatoryCode — AHJ-Directive — Prescriptive | NM CID/NM DOH joint pre-application determination. FGI 2022 confirmed. AHC occupancy confirmed. NM-001 through NM-004 amendments applicable. NM-004 introduces new PIR requirement (exam room 120 NSF).
10 | Geotechnical Consultant Geotechnical Report SGA-2025-0158 — June 6, 2025 | Geotechnical Report | Final | 2025-06-06 | 2025-06-06 | Single-pass | v1.5 | 2 | 108 | 2 NEW (PIR foundation system VE-01, PIR seismic SDC C) · Status update: GR-0020 → GOVERNING (OVERDUE cleared) · VE-01 activated | GeotechnicalReport — Technical | Site Class C confirmed vs. SDC D assumption. VE-01 saves $180K–$340K. SDC C less restrictive. No dewatering required. GR-0020 CLOSED.
11 | Heritage Health Campus Owner Written Design Directives HHC-ODD-001 — June 13, 2025 | Owner Written Design Directives | HHC-ODD-001 | 2025-06-13 | 2025-06-13 | Single-pass | v1.6 | 3 | 111 | 3 NEW (PIR MRI design basis, PIR LASER infrastructure, BCR generator cost allocation) · Status closures: GR-0002, GR-0018, GR-0029, GR-0033, GR-0039, GR-0098, GR-0099, GR-0100 → GOVERNING · CF-001, CF-002, CF-004 RESOLVED | OwnerDirective — Binding | HHC-ODD-001 five directives: MRI vendor (Siemens MAGNETOM Altea confirmed), records storage eliminated, PT LASER confirmed, 145 units confirmed, generator allocation resolved.
12 | Architect of Record (AOR) SD Outline Specifications HHC-SPEC-SD-001 — July 11, 2025 | SD Outline Specifications | HHC-SPEC-SD-001 | 2025-07-11 | 2025-07-11 | Single-pass | v1.7 | 3 | 114 | 3 NEW (RCR submittal protocol, OMR O&M closeout, RCR BIM coordination) | ProjectSpecification — OwnerDirective | 50% SD outline specs Divs 01/11/22/23/26. Code basis confirmed. Submittal requirements and BIM coordination protocol established.
13 | Architect of Record (AOR) 50% SD BIM Coordination Issues Log Rev 0.5 — July 11, 2025 | 50% SD BIM Coordination Issues Log | Rev 0.5 | 2025-07-11 | 2025-07-11 | Single-pass | v1.8 | 4 | 118 | 4 NEW (PIR Zone IV duct, PIR PT column, PIR Level 3 FTC, PIR EES conduit) · CF-007, CF-008 added | BIMCoordinationLog — Technical | 12 clash issues: 2 CRITICAL (register impact), 4 HIGH, 4 MEDIUM, 2 LOW. Two new conflicts: CF-007 PT column, CF-008 Zone IV duct + EES conduit.
14 | Cornerstone Construction CMAR Constructability Review SC-HHC-CR-SD-001 — July 18, 2025 | CMAR Constructability Review | SC-HHC-CR-SD-001 | 2025-07-18 | 2025-07-18 | Single-pass | v1.9 | 4 | 122 | 4 NEW (PIR MRI delivery opening, SMR gas service permit, PIR generator pad DP, SMR elevator engagement DP) · 2 new DECISION-PENDING | ConstructabilityReview — CMAR | 3 critical items: MRI delivery window, PT slab/Level 3 interface, generator pad. Elevator 52–64 week lead identified. Gas service concurrent permit required.
15 | Cost Consultant 50% SD Cost Estimate — July 18, 2025 | 50% SD Cost Estimate | July 18, 2025 | 2025-07-18 | 2025-07-18 | Single-pass | v2.0 | 2 | 124 | 2 NEW (BCR SD TPC reconciliation, BCR TI utilization tracking) | CostEstimate — Owner | SD estimate $67.387M vs. $68M TPC ceiling. $613K contingency. TI estimate $13.473M vs. $14.2M ceiling. $727K TI remaining. VE-01 savings applied.

## Gate2_Validation
HERITAGE HEALTH CAMPUS · GATE 2 WORKBOOK INTEGRITY VALIDATION · v2.0 · PRE-RIR GENERATION CHECK
Test ID | Test Name | Sheet(s) Tested | Rule Summary | Formula / Check | Result
T1 | Total active requirement count consistency | Requirements_Register · Summary_Sheet | Count of GOVERNING + DECISION-PENDING + CONFLICT-PENDING on register must equal Total Active Requirements on Summary_Sheet. |  | PASS
T2 | DECISION-PENDING count matches across sheets | Requirements_Register · Decision_Register · Summary_Sheet | Count of DECISION-PENDING on register must equal rows in Decision_Register AND Summary_Sheet value. |  | PASS
T3 | DecisionType taxonomy compliance | Requirements_Register · Decision_Register | Every DECISION-PENDING record's DecisionType must be one of: TBD-UNRESOLVED, CONDITIONAL, EMBEDDED-CHOICE, SHOULD-LANGUAGE. Zero non-compliant records. |  | PASS
T4 | Conflict cross-sheet linkage | Conflict_Detection_Summary · Requirements_Register | Every CF-XXX in Requirements_Register[ConflictRefs] must exist in Conflict_Detection_Summary. ConflictType must use Doc 3 vocabulary. No duplicate CF IDs. | Cross-reference: every ConflictRef value in RR resolves to a CF row. UNIQUE check on CF IDs. ConflictType IN (ParameterConflict, ScopeConflict, AuthorityConflict, MethodConflict, SequenceConflict). | PASS
T5 | Decision deadline integrity | Decision_Register | Every DECISION-PENDING record has populated DecisionDeadline. Past-deadline records flagged Overdue. |  | PASS
T6 | Lineage Log continuity | Document_Lineage_Log | EntryNumbers sequential 1-N with no gaps. RegisterVersionAfter, ProcessingDate, DocumentIssueDate all populated. Version values non-decreasing. |  | PASS
T7 | Critical-impact verification coverage | Requirements_Register | Every Critical record has populated VerificationMethod AND VerificationAuthority fields. |  | PASS
T8 | Critical-impact concentration ceiling | Requirements_Register | Critical records ≤ 30% of total active requirements. Breach requires disclosure in Section 3 View 4 but does NOT block RIR generation. |  | PASS — verify at generation
T9 | Source document traceability | Requirements_Register · Document_Lineage_Log | Every distinct SourceDocument value in the register must appear in Document_Lineage_Log. No ghost document references. | Cross-reference: every distinct Requirements_Register[SourceDocument] value must resolve to Document_Lineage_Log[DocumentName]. ← Zero unresolved references. | PASS
T10 | Decision Closure Memo audit trail | Decision_Register | N/A for Baseline/Cycle 1. For Cycle 2+: every item where DecisionStatus changed to Resolved since prior cycle must cite a DCM-XXX-NNN identifier. |  | N/A — Baseline Run
✓ GATE 2 DISPOSITION: CLEAR FOR RIR GENERATION · 9/10 TESTS PASS · 1 N/A (T10 — Baseline Run) · T5 REVIEW: 3 overdue DP items flagged

## Verification_Matrix
HERITAGE HEALTH CAMPUS · VERIFICATION MATRIX · v2.0 · © 2026 GALLANT PROJECT SOLUTIONS LLC
Req ID | Requirement Statement (Summary) | Criticality | Verification Method | Verification Authority | Applicability | Status | Notes
GR-0001 | The clinic shall provide primary care services supporting a minimum of 60 scheduled patient encounters per operating day... | High | Test | Northstar Clinical Operations — throughput simulation at 60% DD | Floors 1–2, Northstar clinical TI | GOVERNING | 16 exam rooms required per program
GR-0002 | The clinic shall provide medical imaging services including one Class 1 diagnostic radiography room and one Class 2 MRI ... | Critical | Inspection | Northstar Biomedical Engineering — equipment installation verified | Floors 1–2, Imaging Suite | GOVERNING | OAI-001: MRI vendor under active evaluation — Siemens vs. GE. Structural point l
GR-0003 | The clinic shall provide physical therapy services in a dedicated suite containing minimum 4 open gym treatment stations... | High | Inspection | Northstar Clinical Operations — space program verification | Floors 1–2, PT Suite | GOVERNING | OAI-005: PT equipment plan not yet provided. LASER unit and traction table added
GR-0004 | The clinic shall achieve Joint Commission Ambulatory Health Care (TJC AHC) accreditation on Day 1 of operations. | Critical | Demonstration | TJC AHC accreditation survey result | Floors 1–2, Northstar clinical TI | GOVERNING | All RCR requirements in this register trace to TJC AHC accreditation as the top-
GR-0005 | Primary care patient reception shall have direct, unobstructed visual sightlines to the patient waiting area. No interve... | Moderate | Inspection | Architect of Record (AOR) — SD floor plan review and field verification | Primary Care Suite, Floor 1 | GOVERNING | Direct safety requirement. Relates to SLR-001 access control and TJC RQ-024 work
GR-0006 | Patient waiting shall be provided in two separate designated zones: primary care waiting (minimum 20 seats) and imaging ... | Moderate | Inspection | Architect of Record (AOR) — seat count and zone separation at SD | Floors 1–2, Northstar clinical TI | GOVERNING | Two zones required; combined zone is not acceptable.
GR-0007 | The clinic shall include two dedicated telemedicine rooms with integrated AV equipment, high-bandwidth data, and acousti... | Moderate | Test | Acoustic subconsultant — field measurement at commissioning | Floors 1–2, Telemedicine Rooms | GOVERNING | AV equipment is OFE by Northstar. Infrastructure (conduit, power, data) in TI scop
GR-0008 | All clinical spaces shall prevent inadvertent disclosure of PHI through acoustic means. Conversations in exam rooms shal... | High | Test | Acoustic subconsultant — field measurement at commissioning | Floors 1–2, all clinical spaces | GOVERNING | HIPAA is a federal regulatory requirement. Reinforces TJC RQ-017 acoustic isolat
GR-0009 | Task lighting in all exam rooms, procedure rooms, and treatment rooms shall provide a minimum of 50 footcandles at work ... | Moderate | Test | MEP Engineer of Record (MEP-EOR) (Electrical) — illuminance measurement at commissioning | All exam rooms, treatment rooms, procedure rooms | GOVERNING | 50 fc is IES healthcare standard. Tunable white enables clinical assessment at a
GR-0010 | Clinical exam rooms shall achieve minimum 6 total air changes per hour (ACH) with minimum 2 outdoor air ACH. No recircul... | High | Test | MEP Engineer of Record (MEP-EOR) — TAB report at commissioning | All exam rooms, clinical zones | GOVERNING | ASHRAE 170 compliance is a TJC AHC accreditation requirement per RQ-009.
GR-0011 | Isolation room shall achieve minimum 12 total ACH with minimum 2 OA ACH, maintained negative pressure relative to adjace... | Critical | Test | MEP Engineer of Record (MEP-EOR) — TAB + pressure differential test at commissioning | Isolation Room, Floor 1 | GOVERNING | Life safety and infection control. Negative pressure failure = patient and staff
GR-0012 | MRI magnet room temperature shall be maintained 65–72°F year-round with RH 30–60% year-round. MRI equipment room shall b... | High | Test | MEP Engineer of Record (MEP-EOR) — 30-day trending post-commissioning | MRI Magnet Room + Equipment Room | GOVERNING | 24/7 cooling failure = MRI shutdown. Critical for equipment protection and patie
GR-0013 | Domestic hot water shall be maintained at minimum 110°F at the point of use at all clinical handwashing stations. Thermo... | High | Test | MEP Engineer of Record (MEP-EOR) — temperature measurement at commissioning | All clinical handwashing stations, Floors 1–2 | GOVERNING | Legionella prevention. ASSE 1070 valves required at point of use to prevent scal
GR-0014 | UPS backup power for PACS workstations and IT/server room shall provide minimum 30-minute runtime at full design load. | Moderate | Test | MEP Engineer of Record (MEP-EOR) — UPS runtime test at commissioning | IT Server Room | GOVERNING | 30-minute runtime protects in-flight PACS studies during power interruption. OFE
GR-0015 | PT hydrotherapy whirlpool area shall have dedicated 200A electrical service, waterproof floor-to-ceiling tile, and floor... | High | Inspection | AOR / MEP-EOR — field verification at substantial completion | PT Hydrotherapy Area | GOVERNING | Whirlpool unit weight 900 lbs full. Structural slab must be rated for 150 psf +
GR-0016 | Acoustic separation between exam rooms sharing a common wall shall achieve minimum STC 45. Acoustic separation between e... | High | Analysis + Test | Acoustic subconsultant — calculation at DD + field measurement at commissioning | All exam room partitions, Floors 1–2 | GOVERNING | HIPAA and TJC accreditation requirement. See also GR-0008 (HIPAA FR) and RCR-015
GR-0017 | Owner Program Criteria Rev. 2 shall be issued and accepted as the governing clinical program document prior to Schematic... | Low | Inspection | Gallant / Owner — document in project record dated Dec 10, 2024 | Pre-SD, pre-design phase | GOVERNING | COMPLETE — OPC Rev. 2 issued December 10, 2024.
GR-0018 | MRI model and vendor shall be confirmed in writing by Northstar Biomedical Engineering no later than June 13, 2025, before... | Critical | Inspection | Gallant — written vendor confirmation in project record | Pre-SD gate | GOVERNING | Gate blocker. Siemens vs. GE under active evaluation. Structural point load: Sie
GR-0019 | ICRA shall be completed by Northstar infection preventionist and transmitted to A/E no later than June 27, 2025, before 50... | Critical | Inspection | Gallant — ICRA document in project record with A/E receipt confirmation | Pre-SD gate | DECISION-PENDING | Gate blocker. ICRA not received. HVAC zone boundaries cannot be finalized withou
GR-0020 | Geotechnical investigation report shall be received from Geotechnical Consultant prior to 50% SD structural narrati... | High | Inspection | Gallant / SER — report in project record; structural narrative references confirmed Site Class | Pre-50% SD | GOVERNING | OVERDUE. Report authorized December 2024. Not yet received. Site Class D assumed
GR-0021 | AHJ pre-application inquiry to NM DOH confirming applicable FGI edition and AHC occupancy classification shall be submit... | Critical | Inspection | Gallant — pre-application and AHJ response in project record | Pre-SD gate | GOVERNING | DF-NEW-001 active: NM DOH on FGI 2018, not 2022. AHC occupancy unconfirmed. 8 ft
GR-0022 | Generator procurement shall be initiated no later than October 31, 2025 (30% DD milestone). Procurement shall not begin ... | Critical | Inspection | Gallant / Heritage PM — purchase order in project record by October 31, 2025 | 30% DD gate | DECISION-PENDING | 20–28 week procurement lead. If not ordered by October 2025, generator cannot ar
GR-0023 | RF shielding specialty contractor shall be engaged no later than October 31, 2025 (30% DD). RF shielding engagement shal... | High | Inspection | Gallant — RF shielding contract in project record by October 31, 2025 | 30% DD gate | DECISION-PENDING | 12-week minimum lead. Shielding vendor and spec depend on confirmed MRI vendor p
GR-0024 | MRI magnet shall be set in final installed position before final wall enclosure of the MRI magnet room. Wall enclosure s... | Critical | Inspection | CMAR Superintendent — field report and photographs dated prior to wall enclosure | MRI Magnet Room — construction phase | GOVERNING | If wall enclosure precedes MRI delivery, demolition required to install magnet.
GR-0025 | Primary electrical service to the clinical tenant shall be energized no later than March 2027, providing minimum 90 days... | High | Inspection | Utility / Electrical Sub — energize confirmation in project record; date verified against commissioning schedule | Construction phase | GOVERNING | 90-day minimum between energize and commissioning is consistent with industry pr
GR-0026 | 50% SD deliverables including initial BOD narrative shall be submitted by A/E to Owner and Gallant no later than July 11... | High | Inspection | Gallant / Owner — Procore transmittal record dated on or before July 11, 2025 | SD Phase | GOVERNING | BOD becomes Document 8 in the register. RIR Cycle 1 follows within 14 days.
GR-0027 | Total Project Cost shall not exceed $68,000,000 Board-authorized TPC. Variances exceeding 5% require written Board re-au... | Critical | Analysis | Heritage Cost Consultant — third-party estimate at 60% DD and 90% CD | All project phases | GOVERNING | Current estimate $72M exceeds $68M ceiling by $4M (5.9%). VE-01 and generator co
GR-0028 | Clinical TI construction cost shall not exceed $14,200,000 TI Allowance per executed NNN lease Exhibit D. | Critical | Analysis | Heritage Cost Consultant — TI estimate at 60% DD reconciled against TI Allowance | Clinical TI phases | GOVERNING | Binding per executed lease. Scope additions above TI Allowance require joint wri
GR-0029 | Generator scope allocation (200kW base building vs. 350kW combined EES minimum) shall be assigned in writing between Her... | Critical | Inspection | Gallant / Owner — written memo in project file before 50% SD gate | Pre-50% SD | GOVERNING | CONFLICT-C003 active. OPC estimates 150kW clinical; Programming Doc base buildin
GR-0030 | DD cost estimate shall be reconciled against BCR-001. If variance exceeds 5%, A/E shall prepare VE options log for Owner... | High | Analysis | Heritage Cost Consultant — DD estimate + variance report | 60% DD gate | GOVERNING | VE-01 potential savings $180K–$340K pending geotech confirmation of Site Class C
GR-0031 | Clinical tenant improvement shall achieve total 24,000 GSF across Floors 1 and 2. A/E shall report any deviation from GS... | High | Analysis | Architect of Record (AOR) — area takeoff at 50% SD verified against 24,000 GSF | SD Phase | GOVERNING | 13,740 NSF target with 22% gross-up = 24,000 GSF. Deviation from GSF target must
GR-0032 | Exam rooms shall provide minimum 100 NSF clear floor area exclusive of toilet rooms and casework. Four accessible exam r... | High | Inspection | Architect of Record (AOR) — dimension verification at SD floor plan and field measurement | All exam rooms | GOVERNING | FGI 2022 minimum. 4 accessible rooms require 140 NSF for height-adjustable table
GR-0033 | MRI suite minimum net areas: Magnet Room 700 NSF; Equipment Room 200 NSF (NOTE: GE SIGNA option requires 240 NSF — see O... | High | Inspection | Architect of Record (AOR) — area takeoff at SD + field measurement | MRI Suite, Floor 2 | GOVERNING | CONFLICT-C002 active: OPC programs 200 NSF equipment room; GE SIGNA option requi
GR-0034 | PT open gym shall provide minimum 1,200 NSF with minimum 10-foot clear ceiling height. No structural columns shall intru... | High | Inspection | AOR + SER — area, ceiling height, and column-free verified at SD | PT Suite | GOVERNING | Column-free requirement may affect structural framing design on Level 2 and abov
GR-0035 | Clinical patient corridors on Floors 1 and 2 shall be minimum 8 feet (96 inches) clear width. Staff-only and back-of-hou... | Critical | Inspection | Architect of Record (AOR) — dimension verification at SD floor plan and field measurement | Floors 1 and 2 | GOVERNING | DF-001: AHC occupancy assumed pending AHJ confirmation per GR-0042. 8-ft corrido
GR-0036 | Dedicated AHUs serving the clinical component shall be physically and ductwork-separated from residential and retail HVA... | High | Inspection | MEP Engineer of Record (MEP-EOR) — verified at DD mechanical drawings and field inspection | Clinical AHU mechanical room, Floors 1–2 | GOVERNING | CONFLICT-C003 active: OPC requires dedicated clinical AHUs; Exhibit D silent on
GR-0037 | A separate domestic water riser shall serve clinical Floors 1 and 2. An isolation valve accessible without entering clin... | Moderate | Inspection | MEP Engineer of Record (MEP-EOR) — verified at field inspection at substantial completion | Clinical floors water riser location | GOVERNING | Isolation valve accessibility is critical for maintenance and emergency shutoff
GR-0038 | Medical gas rough-in (O₂ outlet + vacuum outlet) shall be provided at minimum: isolation room (1 each), MRI patient prep... | High | Inspection | MEP Engineer of Record (MEP-EOR) — field verification at rough-in and substantial completion | Isolation room + MRI prep/recovery bays | DECISION-PENDING | OAI-004: Northstar clinical director to confirm whether additional medical gas loc
GR-0039 | MRI magnet room structural design shall accommodate the magnet point load with a dedicated vibration isolation system. S... | Critical | Analysis | Structural Engineer of Record (SER) — structural calculations submitted at 30% DD confirming point load design | MRI Magnet Room structural elements | GOVERNING | CONFLICT-C004 active: Equipment Schedule lists both Siemens (7,700 lb) and GE (8
GR-0040 | PT hydrotherapy whirlpool area structural slab shall be rated for minimum 150 psf plus water load of installed unit (EQ-... | High | Inspection | SER — calculation at 30% DD; waterproof membrane inspection at substantial completion | PT Hydrotherapy Area | GOVERNING | 900 lb at full load. Structural engineer must confirm slab capacity at 30% DD na
GR-0041 | All OFE items in Equipment Schedule v1.0 shall be reflected in A/E Construction Documents with confirmed facility input ... | High | Inspection | Architect of Record (AOR) — OFE facility input drawings in 50% CD submittal | All clinical spaces, Floors 1–2 | GOVERNING | Equipment Schedule v1.0 lists 56 items. Each requires facility inputs in applica
GR-0042 | The clinic shall comply with all Joint Commission Ambulatory Health Care accreditation standards applicable to a new fac... | Critical | Demonstration | TJC AHC accreditation survey result — Day 1 | Floors 1–2, all clinical spaces | GOVERNING | Top-level accreditation requirement. All RCR requirements in sections §1–§6 of T
GR-0043 | The clinical facility design shall comply with the applicable edition of FGI Guidelines for Design and Construction of O... | High | Inspection | AOR — AHJ written confirmation of applicable edition in project record before 50% SD | Pre-50% SD | GOVERNING | DF-NEW-001: NM DOH not confirmed to have adopted FGI 2022. Kickoff meeting ident
GR-0044 | Floors 1–2 clinical occupancy shall be classified as AHC per NFPA 101 Chapter 20. Classification shall be confirmed with... | Critical | Inspection | AHJ — written occupancy confirmation in project record | Floors 1–2 | GOVERNING | DF-001: AHC assumed. If AHJ confirms Group B, corridor widths change from 8 ft t
GR-0045 | Clinical areas shall comply with NFPA 99 (2021) for medical gas systems, Category 1 EES, equipment grounding in all pati... | Critical | Test + Inspection | MEP Engineer of Record (MEP-EOR) — NFPA 99 compliance matrix at 90% CD + commissioning functional tests | All clinical areas | GOVERNING | Category 1 EES requires generator backup for clinical loads. See GR-0029 (BCR-00
GR-0046 | Clinical occupancy egress shall comply with NFPA 101 Chapter 20. Exit travel distance shall not exceed 150 ft. Minimum 2... | Critical | Analysis + Inspection | Architect of Record (AOR) — egress travel distance at SD + AHJ final acceptance | Floors 1–2 | GOVERNING | DF-003: shared egress stairs between clinical and residential occupancies — stai
GR-0047 | Clinical component shall have full automatic sprinkler protection per NFPA 13. Separate sprinkler risers shall serve cli... | Critical | Inspection | Fire Protection Engineer — sprinkler permit drawings + AHJ final acceptance | Floors 1–2 (clinical riser) + Floors 3–7 (residential riser) | GOVERNING | Separate risers ensure clinical sprinkler system can be isolated and maintained
GR-0048 | Imaging suite shall include one Class 1 diagnostic radiography room and one Class 2 imaging room per FGI 2022 §2.3. Lead... | High | Analysis + Inspection | Northstar (radiation physicist report) + AOR (shielding in CDs) | Imaging Suite, Floor 2 | GOVERNING | Radiation physicist engagement required for X-ray shielding. RF shielding by spe
GR-0049 | MRI siting shall comply with ACR Technical Standard for Diagnostic MRI. Zone IV access shall be controlled. Ferromagneti... | Critical | Inspection | AOR — zone diagram in CDs; access control verified at commissioning | MRI Suite, Floor 2 | GOVERNING | ACR zone diagram must appear in CDs. Zone III card reader or keypad required per
GR-0050 | Floor/ceiling assembly between Level 2 clinical and Level 3 residential shall achieve minimum STC 60 / IIC 55. Post-tens... | High | Analysis + Test | Acoustic subconsultant — calculation at DD + field measurement at commissioning | Level 2 slab / Level 3 floor assembly | GOVERNING | PT flat plate alone insufficient per BOD narrative. Acoustic overlay adds cost (
GR-0051 | Hand-washing sinks shall be provided in every exam room, treatment room, triage room, and isolation room. Placement gove... | High | Inspection | AOR — ICRA governs placement; field verification at substantial completion | All clinical rooms | DECISION-PENDING | Conditional on ICRA completion per GR-0019. ICRA not yet received — final sink p
GR-0052 | Clinical areas shall comply with ANSI/ASHRAE/ASHE Standard 170 (2021) ventilation requirements. HVAC design shall meet m... | High | Test | MEP Engineer of Record (MEP-EOR) — TAB report demonstrating ASHRAE 170 compliance at commissioning | All clinical areas | GOVERNING | TJC AHC accreditation requires ASHRAE 170 compliance. Non-compliance at commissi
GR-0053 | A fluid disposal sink (hopper/clinical sink) shall be provided in primary care soiled utility room and imaging soiled ut... | Moderate | Inspection | AOR — field verification at SD floor plan and substantial completion | Primary Care Soiled Utility + Imaging Soiled Utility | GOVERNING | FGI 2022 mandatory requirement. Two locations confirmed per OPC §4.3.
GR-0054 | All clinical spaces shall comply with 2010 ADA Standards for Accessible Design. Minimum 60-in. turning radius in all exa... | High | Inspection | AOR — ADA compliance review at SD + field measurement at substantial completion | All clinical spaces | GOVERNING | Federal law requirement. 4 accessible exam rooms require 140 NSF per GR-0032.
GR-0055 | Patient toilet rooms shall be provided at minimum 1 per 6 exam rooms per FGI 2022 §2.1-3.2. All accessible. One with bar... | High | Inspection | AOR — toilet room count and clearances at SD floor plan | Floors 1–2 | GOVERNING | 1:6 ratio means 3 toilet rooms minimum for 16 exam rooms. OPC programs 3 accessi
GR-0056 | Clinical floors shall be served by Category 1 Essential Electrical System per NFPA 99. Dedicated ATS for clinical EES, s... | Critical | Test | MEP Engineer of Record (MEP-EOR) (Electrical) — EES functional test at commissioning | Clinical Floors 1–2 | DECISION-PENDING | Conditional on BCR-003 resolution. 350kW generator required for NFPA 99 Category
GR-0057 | The building shall comply with ASHRAE 90.1-2019 as adopted by the City of Albuquerque. Energy compliance report shall be... | Moderate | Analysis | MEP Engineer of Record (MEP-EOR) — energy compliance report at 90% CD | All building occupancies | GOVERNING | City of Albuquerque has adopted ASHRAE 90.1-2019. Compliance demonstration requi
GR-0058 | PT hydrotherapy area shall have waterproof membrane beneath all floor and wall tile finishes, extending minimum 18 in. a... | Moderate | Inspection | AOR / Owner's Rep — membrane inspection before tile installation | PT Hydrotherapy Area | GOVERNING | Critical construction quality requirement. Membrane must be inspected and approv
GR-0059 | Floor drains shall be provided in: PT hydrotherapy area, primary care soiled utility room, imaging soiled utility room, ... | Low | Inspection | MEP Engineer of Record (MEP-EOR) / AOR — field verification at rough-in | PT hydrotherapy + soiled utilities + janitor closets | GOVERNING | Standard clinical plumbing requirement. 5 locations confirmed.
GR-0060 | Controlled access shall be provided at the clinical suite entry from the shared building lobby on each clinical floor. C... | High | Demonstration | MEP Engineer of Record (MEP-EOR) — access control functional test at commissioning | Clinical entry points, Floors 1 and 2 | GOVERNING | Integration with Heritage base building system requires early coordination with
GR-0061 | AHC occupancy egress shall comply with NFPA 101 Chapter 20. Exit travel distance not exceeding 150 ft. Minimum 2 enclose... | Critical | Analysis + Inspection | AOR — egress travel distance at SD + AHJ final acceptance | Floors 1–2 | GOVERNING | DF-003: shared egress stair pressurization not confirmed at SD. Life safety requ
GR-0062 | Security cameras shall provide coverage of: clinical entry (min 2), primary care waiting (min 2), imaging waiting (min 1... | Moderate | Inspection | MEP Engineer of Record (MEP-EOR) (infrastructure) + Northstar (OFE installation verification) at substantial completion | All clinical areas per coverage plan | GOVERNING | Camera system OFE by Northstar. Infrastructure in TI scope. Coverage plan must be
GR-0063 | MRI Zone III and Zone IV boundaries shall be controlled access at all times per ACR guidelines. Ferromagnetic screening ... | High | Inspection + Demonstration | AOR + MEP-EOR — access control and ferromagnetic screening verified at commissioning | MRI Suite, Floor 2 | GOVERNING | Projectile risk in MRI zone — life safety requirement. Zone diagram is mandatory
GR-0064 | Facility design shall support annual worksite analysis for workplace violence prevention per TJC. Controlled entry, unob... | Moderate | Inspection | AOR — design review with Northstar security at 60% DD | All clinical areas | GOVERNING | TJC accreditation requirement. Annual worksite analysis requires defensible faci
GR-0065 | MRI equipment room shall have dedicated precision cooling providing 24/7 capability independent of building HVAC. Critic... | High | Test | MEP Engineer of Record (MEP-EOR) — 24/7 operation verification and alarm test at commissioning | MRI Equipment Room | GOVERNING | 24/7 cooling failure = MRI shutdown. Critical alarm required. Non-ferrous compon
GR-0066 | IT/server room (PACS server and network core) shall have 24/7 dedicated cooling independent of building HVAC. No overhea... | High | Test | MEP Engineer of Record (MEP-EOR) — 24/7 operation verification at commissioning | IT Server Room | GOVERNING | No overhead water lines = critical infrastructure protection standard. PACS and
GR-0067 | Clinical tenant ATS shall be separate from residential ATS. ATS shall have test provisions accessible without de-energiz... | High | Test + Inspection | MEP Engineer of Record (MEP-EOR) — ATS transfer time test + field inspection at commissioning | Tenant Electrical Room, Level 1 | GOVERNING | Conditional on BCR-003 generator resolution. Test provisions required so NFPA 99
GR-0068 | PACS base infrastructure (conduit, fiber backbone, junction boxes) shall be installed by contractor as TI scope. PACS se... | Moderate | Inspection | MEP Engineer of Record (MEP-EOR) — infrastructure at rough-in; Northstar IT (OFE installation verification) | Imaging Suite + Reading Suite + IT Server Room | GOVERNING | PACS infrastructure is TI scope; PACS hardware is OFE. Coordinate infrastructure
GR-0069 | All filter racks, fan coil units, VAV terminals, and plumbing cleanouts in the clinical component shall be accessible fr... | Moderate | Inspection | Architect of Record (AOR) — 60% DD coordination review and field verification at substantial completion | All clinical MEP equipment locations | GOVERNING | Gallant OMR standard. Failure to provide accessible maintenance routes creates l
GR-0070 | O&M manuals, as-built drawings, and equipment warranties shall be delivered to Northstar facilities management no later th... | Low | Inspection | Owner's Rep — O&M delivery confirmation within 30 days of substantial completion | Project closeout | GOVERNING | Standard closeout deliverable. TJC accreditation survey may require O&M manuals
GR-0071 | All commercial construction within the City of Albuquerque jurisdiction shall comply with the 2021 New Mexico Commercial... | High | Inspection | AHJ (City of Albuquerque / NM CID) — building permit issuance and final inspection | All building occupancies — Heritage Health Campus | GOVERNING | SUPPLEMENT to GR-0042 (TJC AHC accreditation) and GR-0019 (IBC compliance). Conf
GR-0072 | The energy conservation aspects of the Heritage Health Campus commercial construction shall comply with the New Mexico C... | Moderate | Analysis | MEP Engineer of Record (MEP-EOR) — NMCECC compliance report at 90% CD demonstrating compliance with NM-specific energy provisions | All building occupancies | GOVERNING | SUPPLEMENT to GR-0057 (SER-001 ASHRAE 90.1). NMCECC is the AHJ-confirmed governi
GR-0073 | Exit stair and exit access stair construction shall comply with NMCBC Chapter 10 dimensional requirements: riser height ... | Moderate | Inspection | Architect of Record (AOR) — dimensional verification at construction documents and field measurement at substantial completion | All exit stairs, exit access stairs — Heritage Health Campus | GOVERNING | SUPPLEMENT to GR-0061 (SLR-002 egress). Adds specific NM dimensional requirement
GR-0074 | Construction of a new restroom intended for use in a place of public accommodation shall provide for at least one baby c... | Moderate | Inspection | Architect of Record (AOR) — fixture schedule and floor plan verification at SD; field verification at substantial completion | All floors with public toilet facilities — Floors 1–2 (clinical) and lobby | GOVERNING | NEW requirement — not in any prior source document. NM-specific statutory requir
GR-0075 | The 7-story Heritage Health Campus building shall be confirmed as compliant with NMCBC Table 504 maximum allowable heigh... | Moderate | Analysis | Architect of Record (AOR) — code compliance matrix at SD confirming Table 504 compliance for each occupancy group | All building floors — Floors 1–7 | GOVERNING | NEW requirement added from NMCBC source. Type IA unlimited height confirmed. Cod
GR-0076 | Heritage Health Campus shall be constructed as Type IA (unprotected non-combustible) construction per NMCBC Chapter 6. A... | Moderate | Inspection | AHJ (NM CID / Albuquerque Building Dept) — construction type verified at permit review and field inspection | All building floors — Heritage Health Campus | GOVERNING | SUPPLEMENT to GR-0047 (NFPA 13 sprinkler). Confirms Type IA construction basis.
GR-0077 | The Heritage Health Campus parking facility shall provide accessible parking spaces including van-accessible spaces per ... | Moderate | Inspection | Architect of Record (AOR) / Civil Engineer — site plan compliance verification at SD; field verification at substantial completion | Parking structure / Site — Heritage Health Campus | GOVERNING | SUPPLEMENT to GR-0054 (ADA accessibility). Adds NM/NMCBC parking-specific requir
GR-0078 | Mechanical systems shall comply with the New Mexico Mechanical Code (NMMC). Plumbing systems shall comply with the New M... | Moderate | Inspection | MEP Engineer of Record (MEP-EOR) — verify NM code compliance in CD specifications; AHJ mechanical and plumbing permit review | All mechanical and plumbing systems — Heritage Health Campus | GOVERNING | NEW requirement — not explicitly referenced in prior source documents. Critical
GR-0079 | Concrete construction for Heritage Health Campus shall comply with ACI 318 as adopted and referenced in NMCBC Chapter 19... | Low | Analysis | Structural Engineer of Record (SER) — structural calculations reference ACI 318 at 30% DD; field inspection of concrete mix design and curing records during construction | All concrete structural elements | GOVERNING | SUPPLEMENT to GR-0040 (PIR-010 PT hydrotherapy slab). Confirms ACI 318 as govern
GR-0080 | Exit stairs and exit access stairs serving the clinical occupancy (Floors 1–2) and mixed-occupancy egress shall be of no... | Moderate | Inspection | Architect of Record (AOR) — construction type verified at CD specifications and field inspection | All exit stairs — Heritage Health Campus | GOVERNING | SUPPLEMENT to GR-0061 (SLR-002 egress). Clarifies that NM combustible stair exce
GR-0081 | Standard exam rooms shall provide minimum 120 NSF clear floor area exclusive of toilet rooms and fixed casework, per NM ... | Critical | Inspection | Architect of Record (AOR) — dimension verification at SD floor plan and field measurement | All 12 standard exam rooms | GOVERNING | SUPERSEDES GR-0032 for 12 standard exam rooms. Design revision required at SD —
GR-0082 | The Architect of Record shall be licensed to practice architecture in the State of New Mexico prior to A/E NTP. All requ... | Low | Inspection | Owner's Rep — verification of NM license numbers at contract execution; A/E provides license certificate in proposal Tab 1 | A/E NTP | GOVERNING | Architect of Record (AOR) + Interiors confirmed NM licensed. Southwest MEP Engi
GR-0083 | The A/E shall maintain Professional Liability (Errors and Omissions) insurance of $2,000,000 per occurrence / $4,000,000... | Low | Inspection | Owner's Rep — certificate of insurance at contract execution and annually thereafter | A/E Contract duration + 3 years | GOVERNING | Standard commercial A/E insurance requirement. Certificate provided by Thornton
GR-0084 | The A/E shall complete review of all contractor submittals within 14 calendar days of receipt of a complete submittal. I... | Moderate | Test | Owner's Rep — monitor submittal log for compliance with 14-day review cycle | Construction administration phase | GOVERNING | Performance standard binding on A/E. Critical for clinical equipment submittals
GR-0085 | The A/E shall provide written response to all contractor RFIs within 10 calendar days of receipt. | Moderate | Test | CMAR — monitor RFI log for compliance; report to Owner if A/E misses response window | Construction administration phase | GOVERNING | CMAR (Cornerstone Construction) to monitor RFI log. Any RFI overdue by more than 3
GR-0086 | The A/E shall respond in writing to all Gallant Requirements Intelligence™ RIR conflict items and DECISION-PENDING items... | High | Inspection | Gallant Project Solutions LLC — track response dates in register event ledger | All design phases | GOVERNING | Per RFP §II.A: this is a condition of the A/E contract, not advisory. Gallant tr
GR-0087 | The A/E shall issue site observation reports within 3 Business Days of each site visit during the construction administr... | Low | Inspection | Owner's Rep — monitor CA report log | Construction administration phase | GOVERNING | A/E site visits: biweekly minimum during construction; weekly during critical ph
GR-0088 | As-built drawings shall be delivered within 30 calendar days of project completion in the following formats: Revit model... | Moderate | Inspection | Owner's Rep — delivery confirmation with date stamp within 30 days of substantial completion | Project closeout | GOVERNING | SUPPLEMENT to GR-0070 (OMR-006 O&M delivery). Adds specific Revit model delivera
GR-0089 | Navisworks clash detection reports shall be produced and transmitted to the Owner at 50% SD, 60% DD, and 90% CD. Critica... | High | Inspection | Owner's Rep / Gallant — verify clash detection reports in Procore transmittal log at each gate | 50% SD, 60% DD, 90% CD | GOVERNING | First clash detection report delivered July 11, 2025 with the 50% SD package. 12
GR-0090 | The 50% SD Basis of Design narrative shall contain at minimum: (1) occupancy classification and code basis by floor; (2)... | High | Inspection | Gallant — verify BOD completeness against 9-element checklist at RIR Cycle 1 review | 50% SD gate | GOVERNING | SUPPLEMENT to GR-0026 (SMR-010 50% SD deliverable). Adds the specific 9-element
GR-0091 | Payment for each design phase shall be contingent on Owner acceptance of that phase's deliverables, which includes satis... | High | Inspection | Owner's Rep — issue written acceptance letter after Gallant gate review at each milestone | All design phase gates | GOVERNING | This requirement establishes Gallant gate review as a payment condition — not ad
GR-0092 | Acoustic consulting shall be provided as a mandatory A/E subconsultant discipline. Scope shall include: STC 60 / IIC 55 ... | High | Analysis + Test | Acoustic Subconsultant — calculation at DD + field measurement at commissioning | All acoustic separation assemblies | GOVERNING | SUPPLEMENT to GR-0016 (PR-008 exam room acoustic) and GR-0050 (RCR-009 STC 60).
GR-0093 | The A/E shall design and include in the clinical TI construction documents all audio-visual infrastructure required by t... | Moderate | Inspection | MEP Engineer of Record (MEP-EOR) — AV infrastructure in 50% CD rough-in drawings; Northstar IT confirms coverage | 50% CD submittal | GOVERNING | NEW requirement. AV infrastructure is TI scope; AV hardware is OFE. A/E cannot f
GR-0094 | All design submittals shall be transmitted via the Procore project management platform. Heritage PM will issue Procore a... | Low | Inspection | Owner's Rep — confirm Procore transmittal log is current at each phase gate review | All design phases | GOVERNING | SUPPLEMENT to GR-0026 (50% SD submission). Procore is the confirmed submittal tr
GR-0095 | All OFE items from the Northstar Clinic Equipment Schedule v1.0 shall be modeled in Revit by 30% DD based on vendor-confir... | Moderate | Inspection | Owner's Rep / Gallant — verify OFE families with EQ-IDs present in Revit model at 30% DD clash detection run | 30% DD gate | GOVERNING | SUPPLEMENT to GR-0041 (PIR-011). Adds EQ-ID tagging requirement. Equipment famil
GR-0096 | Owner response to design-phase RFIs shall be provided within 10 Business Days of receipt. Heritage PM (Owner's PM) respond... | Moderate | Inspection | A/E (D. Yuen) — monitor Owner RFI response dates via Procore RFI log | All design phases | GOVERNING | SUPPLEMENT to GR-0085 (A/E RFI response 10 calendar days). Establishes Owner-sid
GR-0097 | The 50% SD cost estimate shall carry an explicit escalation allowance reflecting current Albuquerque construction market... | High | Analysis | Cost Consultant — escalation allowance line item in 50% SD cost estimate | 50% SD gate | GOVERNING | SUPPLEMENT to GR-0030. Escalation allowance is now a required line item in all c
GR-0098 | The physical therapy suite shall accommodate a Class IV Therapeutic LASER System requiring: dedicated 20A/120V GFCI-prot... | High | Inspection | Architect of Record (AOR) / MEP-EOR — verified in 50% SD drawings after written confirmation received | PT Suite, Floor 1 | GOVERNING | EQ-CHANGE-001. PT LASER: Summus Class IV or LiteCure LightForce. Budget authorit
GR-0099 | If a ceiling-mounted overhead track system is selected for the motorized traction table, structural blocking and load pa... | High | Inspection | Structural Engineer of Record (SER) — structural blocking shown in 30% DD structural drawings if ceiling track confirmed | PT Private Treatment Rooms, Floor 1 | GOVERNING | EQ-CHANGE-001 Part 2. Conditional on ceiling track selection. If floor-mount con
GR-0100 | The residential unit count (145 units confirmed or 150 units revised) shall be determined by Heritage in writing and tra... | High | Inspection | Gallant — written owner direction in project record by June 13, 2025 | Pre-50% SD | GOVERNING | PROG-CHANGE-001. Developer evaluating 145 → 150 units. CFS framing and load dist
GR-0101 | The base building construction estimate (Cost Consultant, May 8, 2025) of $44,026,000 exceeds the current baselin... | High | Analysis | Cost Consultant — cost estimate reconciled at 50% SD against BCR-001 | 50% SD cost review | GOVERNING | SUPPLEMENT to GR-0027 (BCR-001) and GR-0030 (BCR-004 VE). Establishes the magnit
GR-0102 | NM DOH Office of Facilities Management plan review submission shall occur at 90% CD submittal stage, concurrent with Cit... | Critical | Document Review | Owner's Rep / AOR — NM DOH Reference Number confirming complete application | 90% CD gate (est. March 27, 2026) | GOVERNING | NEW from D9. Critical path: 45–60 day review from March 27, 2026 submission = NM
GR-0103 | An Infection Control Risk Assessment (ICRA) shall be completed and on file with NM DOH prior to permit submission. The I... | High | Document Review | NM DOH / Northstar Infection Control Officer | Pre-permit submission gate | GOVERNING | NEW from D9 NM-001. Infection preventionist not yet engaged — DECISION-PENDING.
GR-0104 | RF shielding specifications for the MRI suite shall be reviewed and approved by NM DOH prior to installation. The RF shi... | High | Document Review + Inspection | NM DOH | Before RF shielding installation | GOVERNING | NEW from D9 NM-002. Supplements GR-0019 (RF shielding contractor engagement). NM
GR-0105 | All standard patient exam rooms in the AHC clinical floors shall provide a minimum of 120 NSF clear floor area exclusive... | Critical | Design Review + Measurement | NM DOH / Architect of Record (AOR) | All 12 standard exam rooms — Floor 1 | GOVERNING | NEW REQUIREMENT from D9 NM-004. Design revision required before SD complete. OPC
GR-0106 | AHC occupancy (Floors 1–2) shall comply with NFPA 101 Chapter 20 egress requirements: maximum 150-foot travel distance t... | Critical | Design Review + Inspection | NM CID / Fire Marshal | Clinical Floors 1–2 | GOVERNING | NEW from D9 §3. Supplements GR-0035 (corridor width). Stair pressurization per I
GR-0107 | The foundation system shall be designed using shallow spread footings or mat foundation per confirmed Site Class C soil ... | High | Design Review + Special Inspection | Geotechnical Consultant / Structural Engineer of Record (SER) | All foundation elements | GOVERNING | NEW from D10. VE-01 confirmed. Cost estimate D15 shows $310K savings applied at
GR-0108 | The structural design shall use confirmed ASCE 7-22 Site Class C seismic parameters: Ss = 0.65g, S1 = 0.25g, SDC C. Stru... | Moderate | Design Review | Structural Engineer of Record (SER) / AHJ | Entire building structural system | GOVERNING | NEW from D10. SDC C less restrictive than SDC D assumption. No cost increase ant
GR-0109 | The MRI suite design shall be based on the confirmed Siemens Healthineers MAGNETOM Altea 1.5T (Product Code XQ26). Desig... | Critical | Design Review + Commissioning | Northstar Biomedical / Siemens Healthineers | MRI suite — Floor 2 | GOVERNING | NEW from D11 Directive 1. Resolves CF-002 (MRI room area) and CF-004 (MRI point
GR-0110 | The PT private treatment room 2 shall include infrastructure for a Class IV Therapeutic LASER system (Summus 12W): dedic... | Moderate | Inspection | Northstar PT Director / AHJ | PT Treatment Room 2 — Floor 1 | GOVERNING | NEW from D11 Directive 3. EQ-CHANGE-001 CLOSED. Cost: $18K TI electrical (D15 li
GR-0111 | Northstar Health System shall fund the generator upsize cost from 200kW to 350kW (estimated $180,000–$260,000) drawn again... | High | Document Review | Cost Consultant / Owner | Project-wide budget | GOVERNING | NEW from D11 Directive 5. BCR-003 (GR-0029) CLOSED. CF-001 RESOLVED. Actual cost
GR-0112 | A complete submittal schedule shall be submitted to Owner within 30 days of Notice to Proceed. Submittals required for a... | Moderate | Document Review | Owner's Rep / Gallant | Construction phase — all critical clinical systems | GOVERNING | NEW from D12 Div 01. Establishes formal submittal protocol.
GR-0113 | O&M manuals, as-built drawings, and equipment warranties shall be delivered to Northstar Health System facilities manageme... | Moderate | Document Review | Northstar Facilities Management / Owner's Rep | All systems — entire building | GOVERNING | NEW from D12 Div 01 §01 78 00. IFC export adds interoperability requirement for
GR-0114 | The A/E team shall maintain a federated BIM model in Autodesk Revit. Clash detection reports using Navisworks are requir... | Moderate | Document Review | Owner's Rep / Gallant | All design disciplines | GOVERNING | NEW from D12 Div 01 §01 31 00. 50% SD clash run completed — D13 BIM Issues Log i
GR-0115 | All supply air ducts entering the MRI Zone IV envelope shall be provided with RF-shielded duct penetrations or rerouted ... | Critical | Design Review + RF Testing | ACR / RF Shielding Contractor | MRI Zone IV boundary — Floor 2 | CONFLICT-PENDING | NEW from D13 BIM-001 CRITICAL clash. CF-008 flagged. Resolution: reroute duct OR
GR-0116 | The PT open gym area shall be column-free for the full 800 SF minimum program area. The structural system shall provide ... | High | Design Review | Structural Engineer of Record (SER) / Northstar PT Director | PT open gym — Floor 2 | CONFLICT-PENDING | NEW from D13 BIM-010. SER to resolve at 30% DD. CF-007 flagged.
GR-0117 | The Level 3 residential floor design shall account for the acoustic floating floor system required by NM DOH Amendment N... | High | Design Review | Architect of Record (AOR) | Level 3 residential — entire floor | GOVERNING | NEW from D13 BIM-002 / D14 CMAR §2.2. Acoustic subconsultant to coordinate with
GR-0118 | All NFPA 99 Category 1 EES circuits shall be routed in physically separate conduit from normal power circuits. Red color... | High | Inspection | AHJ / Cx Agent | All EES circuits — clinical floors | CONFLICT-PENDING | NEW from D13 BIM-009. MEP-EOR to correct conduit routing. Red color coding requir
GR-0119 | Construction documents shall include a temporary MRI delivery opening in the east wall of the imaging suite (minimum 10 ... | Critical | Schedule Review + Field Inspection | CMAR / GC Superintendent | MRI magnet room — Floor 2 | GOVERNING | NEW from D14 CMAR §2.1. Source: Constructability Review only. Not in any design
GR-0120 | The gas service permit application to NM Gas Company shall be submitted concurrently with the building permit, not after... | High | Schedule Review | CMAR / Owner | Generator pad — site plan | GOVERNING | NEW from D14 CMAR §2.3. Generator pad location is DECISION-PENDING (GR-0121). 12
GR-0121 | Generator pad location shall be confirmed in SD site plan drawings before permit submission. Generator exhaust routing r... | High | Design Review | Architect of Record (AOR) / Southwest MEP | Site plan — 1500 Lomas Blvd NE | DECISION-PENDING | NEW from D14 CMAR §2.3. Generator pad location TBD on 50% SD — must be resolved
GR-0122 | Elevator contractor engagement shall begin during SD phase. The 52–64 week lead time for 4-cab, 7-stop commercial elevat... | Critical | Schedule Review | CMAR / Owner | Base building — elevator shafts | DECISION-PENDING | NEW from D14 CMAR §3. Elevator lead time critical path. Shaft dimensions DECISIO
GR-0123 | Total project cost at 50% SD shall be tracked against the $68M TPC ceiling. Current 50% SD estimate: Base Building $30,9... | Critical | Cost Review | Cost Consultant / Owner | Project-wide | GOVERNING | NEW from D15. SD estimate within TPC ceiling but contingency thin. NM-003 acoust
GR-0124 | Clinical TI Allowance utilization at 50% SD: Base TI construction $9,380,000; Medical equipment installation $695,000; C... | Critical | Cost Review | Cost Consultant / Northstar | Clinical TI scope | GOVERNING | NEW from D15. TI within ceiling but $727K remaining is thin given design is only

## Top_Priority_Items
HERITAGE HEALTH CAMPUS · TOP PRIORITY ITEMS · CRITICAL + DECISION-PENDING + CONFLICT-PENDING · v2.0
Req ID | Category | Requirement Statement (Summary) | Status | Criticality | Risk Drivers | Decision Owner | Notes
GR-0056 | Code — Essential Electrical | Clinical floors shall be served by Category 1 Essential Electrical System per NFPA 99. Dedicated ATS... | DECISION-PENDING | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY ¦ HIGH_COST_INFRASTRUCTURE | Owner's PM + Tenant Facilities Lead (per BCR-003) | Conditional on BCR-003 resolution. 350kW generator required
GR-0019 | Infection Control — Schedule | ICRA shall be completed by Northstar infection preventionist and transmitted to A/E no later than June... | DECISION-PENDING | Critical | DECISION_REQUIRED ¦ REGULATORY_APPROVAL | Northstar — Infection Preventionist | Gate blocker. ICRA not received. HVAC zone boundaries cannot
GR-0022 | Procurement — Long Lead | Generator procurement shall be initiated no later than October 31, 2025 (30% DD milestone). Procurem... | DECISION-PENDING | Critical | LONG_LEAD ¦ DECISION_REQUIRED ¦ HIGH_COST_INFRASTRUCTURE | Owner's PM (Heritage) + Tenant Facilities Lead (Northstar) | 20–28 week procurement lead. If not ordered by October 2025,
GR-0023 | Procurement — Long Lead | RF shielding specialty contractor shall be engaged no later than October 31, 2025 (30% DD). RF shiel... | DECISION-PENDING | High | LONG_LEAD ¦ DECISION_REQUIRED ¦ MULTI_DISCIPLINE_COORDINATION | Northstar / GC Preconstruction | 12-week minimum lead. Shielding vendor and spec depend on co
GR-0122 | SMR — Elevator Procurement | Elevator contractor engagement shall begin during SD phase. The 52–64 week lead time for 4-cab, 7-st... | DECISION-PENDING | Critical | LONG_LEAD ¦ DECISION_REQUIRED ¦ SCHEDULE | Architect of Record (AOR) + Structural Engineer of Record (SER) | NEW from D14 CMAR §3. Elevator lead time critical path. Shaf
GR-0051 | Code — Infection Control | Hand-washing sinks shall be provided in every exam room, treatment room, triage room, and isolation ... | DECISION-PENDING | High | REGULATORY_APPROVAL ¦ DECISION_REQUIRED | Northstar Infection Preventionist | Conditional on ICRA completion per GR-0019. ICRA not yet rec
GR-0038 | Plumbing — Medical Gas | Medical gas rough-in (O₂ outlet + vacuum outlet) shall be provided at minimum: isolation room (1 eac... | DECISION-PENDING | High | REGULATORY_APPROVAL ¦ DECISION_REQUIRED | Northstar Clinical Director | OAI-004: Northstar clinical director to confirm whether additi
GR-0121 | PIR — Site / Generator | Generator pad location shall be confirmed in SD site plan drawings before permit submission. Generat... | DECISION-PENDING | High | DECISION_REQUIRED ¦ SCHEDULE | Architect of Record (AOR) / Southwest MEP | NEW from D14 CMAR §2.3. Generator pad location TBD on 50% SD
GR-0115 | PIR — MRI Zone Compliance | All supply air ducts entering the MRI Zone IV envelope shall be provided with RF-shielded duct penet... | CONFLICT-PENDING | Critical | DESIGN_CONFLICT ¦ REGULATORY_APPROVAL |  | NEW from D13 BIM-001 CRITICAL clash. CF-008 flagged. Resolut
GR-0118 | PIR — NFPA 99 EES | All NFPA 99 Category 1 EES circuits shall be routed in physically separate conduit from normal power... | CONFLICT-PENDING | High | LIFE_SAFETY ¦ REGULATORY_APPROVAL |  | NEW from D13 BIM-009. MEP-EOR to correct conduit routing. Red
GR-0116 | PIR — PT Structural | The PT open gym area shall be column-free for the full 800 SF minimum program area. The structural s... | CONFLICT-PENDING | High | STRUCTURAL ¦ DESIGN_CONFLICT |  | NEW from D13 BIM-010. SER to resolve at 30% DD.
GR-0042 | TJC — Accreditation | The clinic shall comply with all Joint Commission Ambulatory Health Care accreditation standards app... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY | — | Top-level accreditation requirement. All RCR requirements in
GR-0024 | Construction Sequencing | MRI magnet shall be set in final installed position before final wall enclosure of the MRI magnet ro... | GOVERNING | Critical | LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION ¦ HIGH_COST_INFRASTRUCTURE | — | If wall enclosure precedes MRI delivery, demolition required
GR-0002 | Clinical — Imaging | The clinic shall provide medical imaging services including one Class 1 diagnostic radiography room ... | GOVERNING | Critical | DECISION_REQUIRED ¦ LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION | Northstar Biomedical Engineering — Biomedical Engineering Lead | OAI-001: MRI vendor under active evaluation — Siemens vs. GE
GR-0018 | Procurement — Long Lead | MRI model and vendor shall be confirmed in writing by Northstar Biomedical Engineering no later than J... | GOVERNING | Critical | DECISION_REQUIRED ¦ LONG_LEAD ¦ MULTI_DISCIPLINE_COORDINATION | Northstar Biomedical Engineering — Biomedical Engineering Lead | Gate blocker. Siemens vs. GE under active evaluation. Struct
GR-0039 | Structural — MRI | MRI magnet room structural design shall accommodate the magnet point load with a dedicated vibration... | GOVERNING | Critical | DECISION_REQUIRED ¦ LONG_LEAD ¦ HIGH_COST_INFRASTRUCTURE ¦ MULTI_DISCIPLINE_COORDINATION | Northstar Biomedical Engineering (via GR-0018) | CONFLICT-C004 active: Equipment Schedule lists both Siemens
GR-0029 | Cost Control — Generator | Generator scope allocation (200kW base building vs. 350kW combined EES minimum) shall be assigned in... | GOVERNING | Critical | DECISION_REQUIRED ¦ HIGH_COST_INFRASTRUCTURE ¦ SCOPE_GAP | Owner's PM (Heritage) + Tenant Facilities Lead (Northstar) | CONFLICT-C003 active. OPC estimates 150kW clinical; Programm
GR-0011 | Mechanical — HVAC Isolation | Isolation room shall achieve minimum 12 total ACH with minimum 2 OA ACH, maintained negative pressur... | GOVERNING | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | — | Life safety and infection control. Negative pressure failure
GR-0027 | Cost Control — Total Project | Total Project Cost shall not exceed $68,000,000 Board-authorized TPC. Variances exceeding 5% require... | GOVERNING | Critical | HIGH_COST_INFRASTRUCTURE ¦ DECISION_REQUIRED | — | Current estimate $72M exceeds $68M ceiling by $4M (5.9%). VE
GR-0045 | Code — NFPA 99 | Clinical areas shall comply with NFPA 99 (2021) for medical gas systems, Category 1 EES, equipment g... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY ¦ HIGH_COST_INFRASTRUCTURE | — | Category 1 EES requires generator backup for clinical loads.
GR-0049 | Code — MRI Standards | MRI siting shall comply with ACR Technical Standard for Diagnostic MRI. Zone IV access shall be cont... | GOVERNING | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | — | ACR zone diagram must appear in CDs. Zone III card reader or
GR-0119 | PIR — MRI Construction Sequencing | Construction documents shall include a temporary MRI delivery opening in the east wall of the imagin... | GOVERNING | Critical | LONG_LEAD ¦ SCHEDULE ¦ STRUCTURAL |  | NEW from D14 CMAR §2.1. Source: Constructability Review only
GR-0004 | Regulatory — Accreditation | The clinic shall achieve Joint Commission Ambulatory Health Care (TJC AHC) accreditation on Day 1 of... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ LIFE_SAFETY | — | All RCR requirements in this register trace to TJC AHC accre
GR-0044 | Code — Occupancy Classification | Floors 1–2 clinical occupancy shall be classified as AHC per NFPA 101 Chapter 20. Classification sha... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | Architect of Record (AOR) (AHJ response) | DF-001: AHC assumed. If AHJ confirms Group B, corridor width
GR-0046 | Life Safety — Egress | Clinical occupancy egress shall comply with NFPA 101 Chapter 20. Exit travel distance shall not exce... | GOVERNING | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | — | DF-003: shared egress stairs between clinical and residentia
GR-0061 | Life Safety — Egress | AHC occupancy egress shall comply with NFPA 101 Chapter 20. Exit travel distance not exceeding 150 f... | GOVERNING | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | — | DF-003: shared egress stair pressurization not confirmed at
GR-0109 | PIR — MRI System Design Basis | The MRI suite design shall be based on the confirmed Siemens Healthineers MAGNETOM Altea 1.5T (Produ... | GOVERNING | Critical | LONG_LEAD ¦ STRUCTURAL |  | NEW from D11 Directive 1. Resolves CF-002 (MRI room area) an
GR-0021 | Regulatory — AHJ Confirmation | AHJ pre-application inquiry to NM DOH confirming applicable FGI edition and AHC occupancy classifica... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | Architect of Record (AOR) — AOR Project Architect | DF-NEW-001 active: NM DOH on FGI 2018, not 2022. AHC occupan
GR-0028 | Cost Control — Clinical TI | Clinical TI construction cost shall not exceed $14,200,000 TI Allowance per executed NNN lease Exhib... | GOVERNING | Critical | HIGH_COST_INFRASTRUCTURE | — | Binding per executed lease. Scope additions above TI Allowan
GR-0035 | Architecture — Circulation | Clinical patient corridors on Floors 1 and 2 shall be minimum 8 feet (96 inches) clear width. Staff-... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY | AOR + NM DOH (AHJ response) | DF-001: AHC occupancy assumed pending AHJ confirmation per G
GR-0047 | Fire Protection — Sprinkler | Clinical component shall have full automatic sprinkler protection per NFPA 13. Separate sprinkler ri... | GOVERNING | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL | — | Separate risers ensure clinical sprinkler system can be isol
GR-0081 | Space Program — NM DOH | Standard exam rooms shall provide minimum 120 NSF clear floor area exclusive of toilet rooms and fix... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ AHJ_DEPENDENCY |  | SUPERSEDES GR-0032 for 12 standard exam rooms. Design revisi
GR-0102 | RCR — NM DOH Review Process | NM DOH Office of Facilities Management plan review submission shall occur at 90% CD submittal stage,... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ SCHEDULE |  | NEW from D9. Critical path: 45–60 day review from March 27,
GR-0106 | SLR — AHC Life Safety | AHC occupancy (Floors 1–2) shall comply with NFPA 101 Chapter 20 egress requirements: maximum 150-fo... | GOVERNING | Critical | LIFE_SAFETY ¦ REGULATORY_APPROVAL |  | NEW from D9 §3. Supplements GR-0035 (corridor width). Stair
GR-0105 | PIR — Exam Room Area | All standard patient exam rooms in the AHC clinical floors shall provide a minimum of 120 NSF clear ... | GOVERNING | Critical | REGULATORY_APPROVAL ¦ DESIGN_CHANGE |  | NEW REQUIREMENT from D9 NM-004. Design revision required bef
GR-0123 | BCR — Cost Tracking | Total project cost at 50% SD shall be tracked against the $68M TPC ceiling. Current 50% SD estimate:... | GOVERNING | Critical | BUDGET |  | NEW from D15. SD estimate within TPC ceiling but contingency
GR-0124 | BCR — TI Cost Tracking | Clinical TI Allowance utilization at 50% SD: Base TI construction $9,380,000; Medical equipment inst... | GOVERNING | Critical | BUDGET |  | NEW from D15. TI within ceiling but $727K remaining is thin